## Class Air Changes
STANDARDS | CLASSIFICATION | NO.AIR CH/HR |  | Term. Filter Coverage |  | Standard/Class | ACH Range | Notes
ISO 14644-4 | ISO 9 | 5 | 15 | 5% | 15% | ISO 14644-1 Class 1 | 500–750 | Ultra-clean (semiconductors)
ISO 14644-4 | ISO 8 | 20 | 60 | 5% | 15% | ISO 14644-1 Class 2–3 | 500–750
ISO 14644-4 | ISO 7 | 60 | 150 | 15% | 25% | ISO 14644-1 Class 4 | 400–750
ISO 14644-4 | ISO 6 | 150 | 240 | 25% | 40% | ISO 14644-1 Class 5 | 240–600 | Sterile manufacturing
ISO 14644-4 | ISO 5 | 240 | 500 | 35% | 70% | ISO 14644-1 Class 6 | 150–240
ISO 14644-4 | ISO 4 | 300 | 600 | 50% | 90% | ISO 14644-1 Class 7 | 60–150
ISO 14644-4 | ISO 3 | 400 | 750 | 60% | 100% | ISO 14644-1 Class 8 | 10–25
ISO 14644-4 | ISO 2 | 500 | 750 | 80% | 100% | ISO 14698 | 20–40 | Biocontamination control
ISO 14644-4 | ISO 1 | 500 | 750 | 80% | 100% | BS 5295 Class 1–4 | 240–600
FDA 209E | Class100K | 12 | 25 |  |  | AFNOR NF S 90-351 | 20–240 | French standard
FDA 209E | Class10K | 30 | 60 |  |  | TGA (Australia) | 240–600 | Based on ISO/GMP
FDA 209E | Class1K | 80 | 130 |  |  | WHO GMP Grades A–D | 20–240 | A–D grades
FDA 209E | Class 100 | 150 | 300 |  |  | JIS B 9920 (Japan) | 10–600 | Similar to ISO
FDA 209E | Class 10 | 180 | 400 |  |  | FDA (US) | 240–600 | Follows ISO/GMP
FDA 209E | Class 1 | 240 | 500 |  |  | EU GMP Grades A–D | 20–240 | Grades A–D
GMP | Grade D (ISO 8 at Rest & Not Defined) | 20 | 40 |  |  | Germany VDI 2083 | 20–600 | Engineering guideline
GMP | Grade C (ISO 7 at Rest & ISO 8 in Oper.) | 60 | 120
GMP | Grade B (ISO 5 at Rest & ISO 7 in Oper.) | 120 | 180
GMP | Grade A (ISO 5 at Rest & ISO 5 in Oper.) | 180 | 240
JIS B 9920 | JIS Class 9 | 10 | 20
JIS B 9920 | JIS Class 8 | 20 | 60
JIS B 9920 | JIS Class 7 | 60 | 120
JIS B 9920 | JIS Class 6 | 120 | 180
JIS B 9920 | JIS Class 5 | 180 | 240
JIS B 9920 | JIS Class 4 | 240 | 350
JIS B 9920 | JIS Class 3 | 350 | 500
JIS B 9920 | JIS Class 2 | 400 | 600
JIS B 9920 | JIS Class 1 | 400 | 600
EU GMP | Grade D (ISO 7 at Rest & ISO 8 in Oper.) | 40 | 80
EU GMP | Grade C (ISO 7 at Rest & ISO 7 in Oper.) | 80 | 120
EU GMP | Grade B (ISO 5 at Rest & ISO 7 in Oper.) | 120 | 180
EU GMP | Grade A (ISO 5 at Rest & ISO 5 in Oper.) | 180 | 240
TGA | 3500 | 15 | 40
TGA | 350 | 40 | 80
TGA | 35 | 80 | 130
TGA | 3.5 | 130 | 300
TGA | 0.35 | 180 | 400
TGA | 0.035 | 240 | 500
BS 5295 | K | 12 | 25
BS 5295 | J | 30 | 80
BS 5295 | G or H | 120 | 180
BS 5295 | E or F | 240 | 350
BS 5295 | D | 350 | 600
BS 5295 | C | 400 | 600
GERMANY VD | 6 | 20 | 60
GERMANY VD | 5 | 60 | 120
GERMANY VD | 4 | 120 | 180
GERMANY VD | 3 | 180 | 240
GERMANY VD | 2 | 240 | 360
GERMANY VD | 1 | 360 | 550
GERMANY VD | 0 | 400 | 600
AFNOR X44101 | 4000000 | 20 | 50
AFNOR X44101 | 400000 | 60 | 120
AFNOR X44101 | 4000 | 120 | 240
NC-Non Classified | 20µ | 5 | 15
NC-Non Classified | 15µ | 5 | 20
NC-Non Classified | 10µ | 10 | 25
NC-Non Classified | 5µ | 15 | 25
NC-Non Classified | 1µ | 15 | 25
NC-Non Classified | No-Filtration | 5 | 10
NC-Non Classified | Positive Pressure | 5 | 10
NC-Non Classified | Exhaust
ISO 14698 | BSL - 1 | 6 | 12
ISO 14698 | BSL - 2 | 10 | 15
ISO 14698 | BSL - 3 | 15 | 20
ISO 14698 | BSL - 4 | 20 | 30
SCHEDULE M | GRADE CLASS A | 80 | 100
SCHEDULE M | GRADE CLASS B | 60 | 80
SCHEDULE M | GRADE CLASS C | 40 | 60
SCHEDULE M | GRADE CLASS D | 20 | 40

## Sheet1
STANDARDS | CLASSIFICATION | NO.AIR CH/HR
ISO 14644-4 | ISO 9 | 5 | 15 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14644-4', 'ISO 9', 5, 15);
ISO 14644-4 | ISO 8 | 20 | 60 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14644-4', 'ISO 8', 20, 60);
ISO 14644-4 | ISO 7 | 60 | 150 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14644-4', 'ISO 7', 60, 150);
ISO 14644-4 | ISO 6 | 150 | 240 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14644-4', 'ISO 6', 150, 240);
ISO 14644-4 | ISO 5 | 240 | 500 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14644-4', 'ISO 5', 240, 500);
ISO 14644-4 | ISO 4 | 300 | 600 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14644-4', 'ISO 4', 300, 600);
ISO 14644-4 | ISO 3 | 400 | 750 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14644-4', 'ISO 3', 400, 750);
ISO 14644-4 | ISO 2 | 500 | 750 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14644-4', 'ISO 2', 500, 750);
ISO 14644-4 | ISO 1 | 500 | 750 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14644-4', 'ISO 1', 500, 750);
FDA 209E | Class100K | 12 | 25 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('FDA 209E', 'Class100K', 12, 25);
FDA 209E | Class10K | 30 | 60 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('FDA 209E', 'Class10K', 30, 60);
FDA 209E | Class1K | 80 | 130 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('FDA 209E', 'Class1K', 80, 130);
FDA 209E | Class 100 | 150 | 300 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('FDA 209E', 'Class 100', 150, 300);
FDA 209E | Class 10 | 180 | 400 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('FDA 209E', 'Class 10', 180, 400);
FDA 209E | Class 1 | 240 | 500 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('FDA 209E', 'Class 1', 240, 500);
GMP | Grade D (ISO 8 at Rest & Not Defined) | 20 | 40 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('GMP', 'Grade D (ISO 8 at Rest & Not Defined)', 20, 40);
GMP | Grade C (ISO 7 at Rest & ISO 8 in Oper.) | 60 | 120 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('GMP', 'Grade C (ISO 7 at Rest & ISO 8 in Oper.)', 60, 120);
GMP | Grade B (ISO 5 at Rest & ISO 7 in Oper.) | 120 | 180 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('GMP', 'Grade B (ISO 5 at Rest & ISO 7 in Oper.)', 120, 180);
GMP | Grade A (ISO 5 at Rest & ISO 5 in Oper.) | 180 | 240 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('GMP', 'Grade A (ISO 5 at Rest & ISO 5 in Oper.)', 180, 240);
JIS B 9920 | JIS Class 9 | 10 | 20 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('JIS B 9920', 'JIS Class 9', 10, 20);
JIS B 9920 | JIS Class 8 | 20 | 60 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('JIS B 9920', 'JIS Class 8', 20, 60);
JIS B 9920 | JIS Class 7 | 60 | 120 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('JIS B 9920', 'JIS Class 7', 60, 120);
JIS B 9920 | JIS Class 6 | 120 | 180 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('JIS B 9920', 'JIS Class 6', 120, 180);
JIS B 9920 | JIS Class 5 | 180 | 240 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('JIS B 9920', 'JIS Class 5', 180, 240);
JIS B 9920 | JIS Class 4 | 240 | 350 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('JIS B 9920', 'JIS Class 4', 240, 350);
JIS B 9920 | JIS Class 3 | 350 | 500 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('JIS B 9920', 'JIS Class 3', 350, 500);
JIS B 9920 | JIS Class 2 | 400 | 600 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('JIS B 9920', 'JIS Class 2', 400, 600);
JIS B 9920 | JIS Class 1 | 400 | 600 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('JIS B 9920', 'JIS Class 1', 400, 600);
EU GMP | Grade D (ISO 7 at Rest & ISO 8 in Oper.) | 40 | 80 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('EU GMP', 'Grade D (ISO 7 at Rest & ISO 8 in Oper.)', 40, 80);
EU GMP | Grade C (ISO 7 at Rest & ISO 7 in Oper.) | 80 | 120 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('EU GMP', 'Grade C (ISO 7 at Rest & ISO 7 in Oper.)', 80, 120);
EU GMP | Grade B (ISO 5 at Rest & ISO 7 in Oper.) | 120 | 180 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('EU GMP', 'Grade B (ISO 5 at Rest & ISO 7 in Oper.)', 120, 180);
EU GMP | Grade A (ISO 5 at Rest & ISO 5 in Oper.) | 180 | 240 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('EU GMP', 'Grade A (ISO 5 at Rest & ISO 5 in Oper.)', 180, 240);
TGA | 3500 | 15 | 40 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('TGA', '3500', 15, 40);
TGA | 350 | 40 | 80 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('TGA', '350', 40, 80);
TGA | 35 | 80 | 130 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('TGA', '35', 80, 130);
TGA | 3.5 | 130 | 300 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('TGA', '3.5', 130, 300);
TGA | 0.35 | 180 | 400 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('TGA', '0.35', 180, 400);
TGA | 0.035 | 240 | 500 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('TGA', '0.035', 240, 500);
BS 5295 | K | 12 | 25 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('BS 5295', 'K', 12, 25);
BS 5295 | J | 30 | 80 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('BS 5295', 'J', 30, 80);
BS 5295 | G or H | 120 | 180 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('BS 5295', 'G or H', 120, 180);
BS 5295 | E or F | 240 | 350 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('BS 5295', 'E or F', 240, 350);
BS 5295 | D | 350 | 600 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('BS 5295', 'D', 350, 600);
BS 5295 | C | 400 | 600 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('BS 5295', 'C', 400, 600);
GERMANY VD | 6 | 20 | 60 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('GERMANY VD', '6', 20, 60);
GERMANY VD | 5 | 60 | 120 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('GERMANY VD', '5', 60, 120);
GERMANY VD | 4 | 120 | 180 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('GERMANY VD', '4', 120, 180);
GERMANY VD | 3 | 180 | 240 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('GERMANY VD', '3', 180, 240);
GERMANY VD | 2 | 240 | 360 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('GERMANY VD', '2', 240, 360);
GERMANY VD | 1 | 360 | 550 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('GERMANY VD', '1', 360, 550);
GERMANY VD | 0 | 400 | 600 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('GERMANY VD', '0', 400, 600);
AFNOR X44101 | 4000000 | 20 | 50 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('AFNOR X44101', '4000000', 20, 50);
AFNOR X44101 | 400000 | 60 | 120 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('AFNOR X44101', '400000', 60, 120);
AFNOR X44101 | 4000 | 120 | 240 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('AFNOR X44101', '4000', 120, 240);
NC-Non Classified | 20µ | 5 | 15 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('NC-Non Classified', '20µ', 5, 15);
NC-Non Classified | 15µ | 5 | 20 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('NC-Non Classified', '15µ', 5, 20);
NC-Non Classified | 10µ | 10 | 25 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('NC-Non Classified', '10µ', 10, 25);
NC-Non Classified | 5µ | 15 | 25 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('NC-Non Classified', '5µ', 15, 25);
NC-Non Classified | 1µ | 15 | 25 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('NC-Non Classified', '1µ', 15, 25);
NC-Non Classified | No-Filtration | 5 | 10 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('NC-Non Classified', 'No-Filtration', 5, 10);
NC-Non Classified | Positive Pressure | 5 | 10 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('NC-Non Classified', 'Positive Pressure', 5, 10);
NC-Non Classified | Exhaust | 0 | 0 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('NC-Non Classified', 'Exhaust', 0, 0);
ISO 14698 | BSL - 1 | 6 | 12 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14698', 'BSL - 1', 6, 12);
ISO 14698 | BSL - 2 | 10 | 15 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14698', 'BSL - 2', 10, 15);
ISO 14698 | BSL - 3 | 15 | 20 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14698', 'BSL - 3', 15, 20);
ISO 14698 | BSL - 4 | 20 | 30 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('ISO 14698', 'BSL - 4', 20, 30);
SCHEDULE M | GRADE CLASS A | 80 | 100 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('SCHEDULE M', 'GRADE CLASS A', 80, 100);
SCHEDULE M | GRADE CLASS B | 60 | 80 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('SCHEDULE M', 'GRADE CLASS B', 60, 80);
SCHEDULE M | GRADE CLASS C | 40 | 60 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('SCHEDULE M', 'GRADE CLASS C', 40, 60);
SCHEDULE M | GRADE CLASS D | 20 | 40 | INSERT INTO tCR_metadata (standard_name, classification_name, acph_min, acph_max) VALUES ('SCHEDULE M', 'GRADE CLASS D', 20, 40);

## Classification
ids | Standards | ISO_14644 | FDA | GMP | JIS_B_9920 | EUGMP | WHO | TGA | BS_5295 | GERMANY_VD | AFNORX44101 | NC -Non Classified
ISO_14644ISO 8Class100K00001 | ISO_14644 | ISO 9 | Class100K | Grade D (ISO 8 at Rest & Not Defined) | JIS Class 9 | Grade D (ISO 7 at Rest & ISO 8 in Oper.) | Asia | 3500 | K |  |  | 20µ
FDAISO 7Class10K00002 | FDA | ISO 8 | Class10K | Grade C (ISO 7 at Rest & ISO 8 in Oper.) | JIS Class 8 | Grade C (ISO 7 at Rest & ISO 7 in Oper.) | Africa | 350 | J | 6 | 4000000 | 15µ
GMPISO 6Class1K00003 | GMP | ISO 7 | Class1K | Grade B (ISO 5 at Rest & ISO 7 in Oper.) | JIS Class 7 | Grade B (ISO 5 at Rest & ISO 7 in Oper.) | North America | 35 | G or H | 5 | 400000 | 10µ
TGAISO 5Class 10000004 | TGA | ISO 6 | Class 100 | Grade A (ISO 5 at Rest & ISO 5 in Oper.) | JIS Class 6 | Grade A (ISO 5 at Rest & ISO 5 in Oper.) | South America | 3.5 | E or F | 4 | - | 5µ
JIS_B_9920ISO 4Class 1000005 | JIS_B_9920 | ISO 5 | Class 10 |  | JIS Class 5 |  | Antartica | 0.35 | D | 3 | 4000 | 1µ
EUGMPISO 3Class 100006 | EUGMP | ISO 4 | Class 1 |  | JIS Class 4 |  | Europe | 0.035 | C | 2 | - | No-Filtration
#REF! | WHO | ISO 3 |  |  | JIS Class 3 |  | Australia |  |  | 1 | - | Positive Pressure
BS_5295ISO 200008 | BS_5295 | ISO 2 |  |  | JIS Class 2 |  |  |  |  | 0 | - | Exhaust
GERMANY_VDISO 100009 | GERMANY_VD | ISO 1 |  |  | JIS Class 1
AFNORX4410100010 | AFNORX44101
NC_Non_Classified00011 | NC_Non_Classified
Filtration Stages
| Air-conditioning System |  |  | 1S | 20 micron filters made out of HDPE media with one side HDPE & other side Al. expanded mesh of efficiency 90%(150 mm thick) for fresh air supply
| Ventilation System |  |  | 1E | 20 micron filters made out of HDPE media with one side HDPE & other side Al. expanded mesh of efficiency 90%(100 mm thick) for Exhaust air.
|  |  |  | 2S | 10 micron filters made out of HLP media with one side HDPE & other side Al. expanded mesh of efficiency 95%(150 mm thick) for fresh air supply
TGA | Adelaide |  |  | 2E | 10 micron filters made out of HLP media with one side HDPE & other side Al. expanded mesh of efficiency 95%(150 mm thick) for Exhaust Air
|  |  |  | 3S | 5 micron filters made out of SNPF media 150GSM with one side HDPE & other side Al. expanded mesh of efficiency 99%(300 mm thick) for fresh air supply
|  |  |  | 3E | 5 micron filters made out of SNPF media 150GSM with one side HDPE & other side Al. expanded mesh of efficiency 99%(300 mm thick) for Exhaust Air
|  |  |  | 4S | 1 micron filters made out of SNPF media 200GSM with one side HDPE & other side Al. expanded mesh of efficiency 99.9%(300 mm thick) for fresh air supply
|  |  |  | 4E | 1 micron filters made out of SNPF media 200GSM with one side HDPE & other side Al. expanded mesh of efficiency 99.9%(300 mm thick) for Exhaust Air
|  |  |  | 5S | 0.3 micron 95% Eff. HEPA filters made out of imported Lydall media with efficiency 95%(300 mm thick) for fresh air supply
|  |  |  | 5E | 0.3 micron 95% Eff. HEPA filters made out of imported Lydall media with efficiency 95%(300 mm thick) for Exhaust Air
|  |  |  | 6S | 0.3 micron 99.97% Eff. HEPA filters made out of imported Lydall media with efficiency 95%(150 mm thick) for Supply Air
|  |  |  | 6E | 0.3 micron 99.97% Eff. HEPA filters made out of imported Lydall media with efficiency 95%(150 mm thick) for Exhaust Air
|  |  |  | 7S | 0.1 micron 99.9995% Eff. ULPA filters made out of imported Lydall media with efficiency 95%(150 mm thick) for Supply Air
|  |  |  | 7E | 0.1 micron 99.9995% Eff. ULPA filters made out of imported Lydall media with efficiency 95%(150 mm thick) for Exhaust Air
ids | Standards | ISO_14644 | FDA | GMP | JIS_B_9920 | EUGMP | WHO | TGA | BS_5295 | GERMANY_VD | AFNORX44101 | NC -Non Classified
ISO_14644ISO 8Class100K00037 | ISO_14644 | ISO 9 | Class100K | Grade D (ISO 8 at Rest & Not Defined) | JIS Class 9 | Grade D (ISO 7 at Rest & ISO 8 in Oper.) | Asia | 3500 | K |  |  | 20µ
FDAISO 7Class10K00038 | FDA | ISO 8 | Class10K | Grade C (ISO 7 at Rest & ISO 8 in Oper.) | JIS Class 8 | Grade C (ISO 7 at Rest & ISO 7 in Oper.) | Africa | 350 | J | 6 | 4000000 | 15µ
GMPISO 6Class1K00039 | GMP | ISO 7 | Class1K | Grade B (ISO 5 at Rest & ISO 7 in Oper.) | JIS Class 7 | Grade B (ISO 5 at Rest & ISO 7 in Oper.) | North America | 35 | G or H | 5 | 400000 | 10µ
TGAISO 5Class 10000040 | TGA | ISO 6 | Class 100 | Grade A (ISO 5 at Rest & ISO 5 in Oper.) | JIS Class 6 | Grade A (ISO 5 at Rest & ISO 5 in Oper.) | South America | 3.5 | E or F | 4 | - | 5µ
JIS_B_9920ISO 4Class 1000041 | JIS_B_9920 | ISO 5 | Class 10 |  | JIS Class 5 |  | Antartica | 0.35 | D | 3 | 4000 | 1µ
EUGMPISO 3Class 100042 | EUGMP | ISO 4 | Class 1 |  | JIS Class 4 |  | Europe | 0.035 | C | 2 | - | No-Filtration
#REF! | WHO | ISO 3 |  |  | JIS Class 3 |  | Australia |  |  | 1 | - | Positive Pressure
BS_5295ISO 200044 | BS_5295 | ISO 2 |  |  | JIS Class 2 |  |  |  |  | 0 | - | Exhaust
GERMANY_VDISO 100045 | GERMANY_VD | ISO 1 |  |  | JIS Class 1
AFNORX4410100046 | AFNORX44101
NC_Non_Classified00047 | NC_Non_Classified

## Input BOD
Zoning Area AHU - 1 Air-Conditioning System
S.No. | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Select Class | ACPH | Chilled water enter C Direct Expansion enter D | Select Standards | Manual Entry for ACPH
1 | Chandrashekar | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
2 | vijay bhasker | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
3 | nimma | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
4 | sahajanand | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
5 | xyz | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
6 | abc | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
7 | excel | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
8 | word | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
9 | java | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
10 | 12345 | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
11 | cvdwvjvq | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
12 | jcvbbvk | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
13 | vbwbvb | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
14 | b cjvjvve | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
15 | ifhiuhfigi | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
16 | hbhwbfb | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | D | FDA | 0 | 12
Zoning Area AHU - 2 Air-Conditioning System
| Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
18 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
19 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
20 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
21 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
22 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
23 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
24 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
25 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
26 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
27 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
28 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
29 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
30 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
31 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
32 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
33 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | C
Zoning Area AHU - 3 Air-Conditioning System
34 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
35 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
36 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
37 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
38 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
39 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
40 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
41 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
42 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
43 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
44 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
45 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
46 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
47 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
48 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
49 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
50 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | C
Zoning Area AHU - 4 Air-Conditioning System
51 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
52 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
53 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
54 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
55 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
56 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
57 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
58 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
59 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
60 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
61 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
62 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
63 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
64 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
65 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
66 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
67 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | C
Zoning Area AHU - 5 Air-Conditioning System
68 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
69 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
70 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
71 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
72 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
73 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
74 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
75 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
76 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
77 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
78 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
79 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
80 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
81 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
82 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
83 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
84 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | C
Zoning Area AHU - 6 Air-Conditioning System
85 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
86 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
87 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
88 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
89 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
90 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
91 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
92 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
93 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
94 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
95 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
96 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
97 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
98 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
99 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
100 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
101 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | C
Zoning Area AHU - 7 Air-Conditioning System
102 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
103 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
104 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
105 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
106 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
107 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
108 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
109 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
110 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
111 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
112 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
113 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
114 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
115 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
116 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
117 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
118 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
Zoning Area AHU - 8 Air-Conditioning System
119 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
120 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
121 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
122 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
123 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
124 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
125 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
126 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
127 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
128 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
129 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
130 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
131 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
132 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
133 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
134 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
135 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
Zoning Area AHU - 9 Air-Conditioning System
136 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
137 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
138 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
139 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
140 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
141 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
142 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
143 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
144 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
145 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
146 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
147 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
148 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
149 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
150 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
151 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
152 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
Zoning Area AHU - 10 Air-Conditioning System
153 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
154 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
155 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
156 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
157 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
158 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
159 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
160 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
161 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
162 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
163 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
164 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
165 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
166 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
167 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
168 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
169 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
Zoning Area AHU - 11 Air-Conditioning System
170 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
171 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
172 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
173 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
174 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
175 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
176 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
177 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
178 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
179 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
180 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
181 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
182 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
183 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
184 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
185 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
186 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
Zoning Area AHU - 12 Air-Conditioning System
187 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
188 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
189 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
190 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
191 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
192 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
193 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
194 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
195 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
196 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
197 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
198 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
199 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
200 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
201 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
202 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
203 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
Zoning Area AHU - 13 Air-Conditioning System
204 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
205 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
206 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
207 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
208 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
209 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
210 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
211 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
212 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
213 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
214 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
215 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
216 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
217 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
218 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
219 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
220 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
Zoning Area AHU - 14 Air-Conditioning System
221 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
222 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
223 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
224 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
225 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
226 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
227 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
228 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
229 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
230 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
231 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
232 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
233 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
234 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
235 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
236 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
237 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
Zoning Area AHU - 15 Air-Conditioning System
238 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
239 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
240 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
241 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
242 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
243 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
244 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
245 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
246 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
247 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
248 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
249 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
250 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
251 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
252 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
253 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
254 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
Zoning Area AHU - 16 Ventilation System
255 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
256 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
257 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
258 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
259 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
260 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
261 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
262 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
263 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
264 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
265 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
266 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
267 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
268 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
269 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
270 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
271 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | C
Zoning Area AHU - 17 Air-Conditioning System
272 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
273 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
274 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
275 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
276 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
277 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
278 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
279 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
280 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
281 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
282 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
283 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
284 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
285 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
286 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
287 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
288 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | C
Zoning Area AHU - 18 Air-Conditioning System
289 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
290 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
291 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
292 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
293 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
294 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
295 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
296 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
297 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
298 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
299 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
300 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
301 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
302 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
303 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
304 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
305 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | C
Zoning Area AHU - 19 Air-Conditioning System
306 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
307 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
308 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
309 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
310 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
311 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
312 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
313 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
314 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
315 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
316 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
317 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
318 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
319 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
320 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
321 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
322 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | C
Zoning Area AHU - 20 Air-Conditioning System
323 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | ACPH
324 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
325 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
326 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
327 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
328 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
329 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
330 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
331 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
332 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
333 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
334 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
335 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
336 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
337 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
338 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C
339 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | C

## Output BOD
Zoning Area AHU - 1 Air-Conditioning System (DX) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
S.No. | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
1 | Chandrashekar | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 | 15750 | W | 125 | 710 | 20 | 8 | 56 | 3 | 224 | 14.1322 | 2 | 94.8756
2 | vijay bhasker | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 |  | 2050
3 | nimma | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 |  | H
4 | sahajanand | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 |  | 2050
5 | xyz | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 |  | L
6 | abc | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 |  | 5900
7 | excel | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5
8 | word | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5
9 | java | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5
10 | 12345 | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 |  | 5500
11 | cvdwvjvq | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5
12 | jcvbbvk | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5
13 | vbwbvb | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5
14 | b cjvjvve | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5
15 | ifhiuhfigi | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5
16 | hbhwbfb | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5
[21 empty] | 172.16 | 1129.3696 | 225.8739 | 22.5874 | 0 | 1.5729 | 15600 | 15600 | 0 | 56 |  | 40 | 56
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
| Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
18 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 96.84 | 762.3245 | 2032.8653 | 203.2865 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
19 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 42.6096 | 335.4228 | 894.4607 | 89.4461 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
20 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 45.192 | 355.7514 | 948.6705 | 94.867 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
21 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 79.086 | 622.565 | 1660.1733 | 166.0173 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
22 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 116.208 | 914.7894 | 2439.4383 | 243.9438 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
23 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 171.7296 | 1351.8554 | 3604.9478 | 360.4948 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
24 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 86.7256 | 682.7039 | 1820.5438 | 182.0544 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
25 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 49.0656 | 386.2444 | 1029.9851 | 102.9985 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
26 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 93.612 | 736.9137 | 1965.1031 | 196.5103 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
27 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 51.648 | 406.5731 | 1084.1948 | 108.4195 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
28 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 40.6728 | 320.1763 | 853.8034 | 85.3803 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
29 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 36.7992 | 289.6833 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
30 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 40.888 | 321.8703 | 858.3209 | 85.8321 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
31 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 54.4456 | 428.5958 | 1142.922 | 114.2922 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
32 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 66.2816 | 521.7688 | 1391.3833 | 139.1383 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
33 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 72.3072 | 569.2023 | 1517.8727 | 151.7873 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 24017.1739 | 2401.7174 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
34 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
35 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 96.84 | 762.3245 | 1905.8112 | 190.5811 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
36 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 42.6096 | 335.4228 | 838.5569 | 83.8557 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! |  | #DIV/0!
37 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 45.192 | 355.7514 | 889.3786 | 88.9379 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! |  | H
38 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 79.086 | 622.565 | 1556.4125 | 155.6412 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! |  | #DIV/0!
39 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 116.208 | 914.7894 | 2286.9734 | 228.6973 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! |  | L
40 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 171.7296 | 1351.8554 | 3379.6385 | 337.9639 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! |  | #DIV/0!
41 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 86.7256 | 682.7039 | 1706.7598 | 170.676 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
42 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 49.0656 | 386.2444 | 965.611 | 96.5611 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
43 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 93.612 | 736.9137 | 1842.2842 | 184.2284 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
44 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 51.648 | 406.5731 | 1016.4326 | 101.6433 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! |  | #DIV/0!
45 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 40.6728 | 320.1763 | 800.4407 | 80.0441 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
46 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 36.7992 | 289.6833 | 724.2083 | 72.4208 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
47 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 40.888 | 321.8703 | 804.6758 | 80.4676 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
48 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 54.4456 | 428.5958 | 1071.4894 | 107.1489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
49 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 66.2816 | 521.7688 | 1304.4219 | 130.4422 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
50 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 72.3072 | 569.2023 | 1423.0057 | 142.3006 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 22516.1005 | 2251.6101 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
51 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
52 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 96.84 | 762.3245 | 1016.4326 | 101.6433 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
53 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 42.6096 | 335.4228 | 447.2304 | 44.723 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
54 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 45.192 | 355.7514 | 474.3352 | 47.4335 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
55 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 79.086 | 622.565 | 830.0867 | 83.0087 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
56 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 116.208 | 914.7894 | 1219.7192 | 121.9719 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
57 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 171.7296 | 1351.8554 | 1802.4739 | 180.2474 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
58 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 86.7256 | 682.7039 | 910.2719 | 91.0272 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
59 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 49.0656 | 386.2444 | 514.9925 | 51.4993 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
60 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 93.612 | 736.9137 | 982.5516 | 98.2552 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
61 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 51.648 | 406.5731 | 542.0974 | 54.2097 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
62 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 40.6728 | 320.1763 | 426.9017 | 42.6902 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
63 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 36.7992 | 289.6833 | 386.2444 | 38.6244 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
64 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 40.888 | 321.8703 | 429.1604 | 42.916 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
65 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 54.4456 | 428.5958 | 571.461 | 57.1461 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
66 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 66.2816 | 521.7688 | 695.6917 | 69.5692 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
67 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 72.3072 | 569.2023 | 758.9364 | 75.8936 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 12008.587 | 1200.8587 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
68 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
69 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 96.84 | 762.3245 | 254.1082 | 25.4108 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
70 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 42.6096 | 335.4228 | 111.8076 | 11.1808 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
71 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 45.192 | 355.7514 | 118.5838 | 11.8584 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
72 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 79.086 | 622.565 | 207.5217 | 20.7522 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
73 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 116.208 | 914.7894 | 304.9298 | 30.493 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
74 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 171.7296 | 1351.8554 | 450.6185 | 45.0618 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
75 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 86.7256 | 682.7039 | 227.568 | 22.7568 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
76 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 49.0656 | 386.2444 | 128.7481 | 12.8748 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
77 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 93.612 | 736.9137 | 245.6379 | 24.5638 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
78 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 51.648 | 406.5731 | 135.5244 | 13.5524 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
79 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 40.6728 | 320.1763 | 106.7254 | 10.6725 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
80 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 36.7992 | 289.6833 | 96.5611 | 9.6561 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
81 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 40.888 | 321.8703 | 107.2901 | 10.729 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
82 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 54.4456 | 428.5958 | 142.8653 | 14.2865 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
83 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 66.2816 | 521.7688 | 173.9229 | 17.3923 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
84 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 72.3072 | 569.2023 | 189.7341 | 18.9734 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 3002.1467 | 300.2147 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
85 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
86 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 96.84 | 762.3245 | 317.6352 | 31.7635 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
87 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 42.6096 | 335.4228 | 139.7595 | 13.9759 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! |  | #DIV/0!
88 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 45.192 | 355.7514 | 148.2298 | 14.823 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! |  | H
89 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 79.086 | 622.565 | 259.4021 | 25.9402 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! |  | #DIV/0!
90 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 116.208 | 914.7894 | 381.1622 | 38.1162 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! |  | L
91 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 171.7296 | 1351.8554 | 563.2731 | 56.3273 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! |  | #DIV/0!
92 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 86.7256 | 682.7039 | 284.46 | 28.446 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
93 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 49.0656 | 386.2444 | 160.9352 | 16.0935 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
94 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 93.612 | 736.9137 | 307.0474 | 30.7047 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
95 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 51.648 | 406.5731 | 169.4054 | 16.9405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0! |  | #DIV/0!
96 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 40.6728 | 320.1763 | 133.4068 | 13.3407 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
97 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 36.7992 | 289.6833 | 120.7014 | 12.0701 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
98 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 40.888 | 321.8703 | 134.1126 | 13.4113 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
99 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 54.4456 | 428.5958 | 178.5816 | 17.8582 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
100 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 66.2816 | 521.7688 | 217.4036 | 21.7404 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
101 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 72.3072 | 569.2023 | 237.1676 | 23.7168 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | D | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 3752.6834 | 375.2683 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
102 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
103 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
104 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
105 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
106 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
107 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
108 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
109 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
110 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
111 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
112 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
113 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
114 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
115 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
116 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
117 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
118 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
119 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
120 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
121 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
122 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
123 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
124 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
125 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
126 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
127 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
128 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
129 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
130 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
131 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
132 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
133 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
134 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
135 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
136 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
137 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
138 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
139 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
140 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
141 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
142 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
143 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
144 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
145 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
146 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
147 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
148 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
149 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
150 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
151 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
152 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
153 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
154 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
155 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
156 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
157 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
158 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
159 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
160 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
161 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
162 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
163 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
164 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
165 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
166 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
167 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
168 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
169 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
170 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
171 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
172 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
173 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
174 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
175 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
176 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
177 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
178 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
179 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
180 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
181 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
182 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
183 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
184 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
185 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
186 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
187 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
188 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
189 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
190 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
191 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
192 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
193 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
194 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
195 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
196 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
197 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
198 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
199 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
200 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
201 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
202 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
203 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
204 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
205 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
206 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
207 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
208 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
209 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
210 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
211 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
212 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
213 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
214 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
215 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
216 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
217 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
218 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
219 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
220 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
221 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
222 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
223 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
224 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
225 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
226 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
227 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
228 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
229 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
230 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
231 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
232 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
233 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
234 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
235 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
236 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
237 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
238 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
239 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
240 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
241 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
242 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
243 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
244 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
245 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
246 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
247 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
248 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
249 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
250 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
251 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
252 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
253 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
254 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
Zoning Area AHU - 16 Ventilation System | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
255 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
256 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 1524.649 | Ambient | Ambient | 1700 | 10 | Ambient | C | Ambient | Ambient | 20000 | W | 150 | 800 | 30 | Amb | 0 | 3 | 0 | 0 | 2 | 0
257 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 670.8455 | Ambient | Ambient | 750 | 6 | Ambient | C | Ambient | Ambient |  | 2900
258 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 711.5028 | Ambient | Ambient | 800 | 6 | Ambient | C | Ambient | Ambient |  | H
259 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 1245.13 | Ambient | Ambient | 1375 | 8 | Ambient | C | Ambient | Ambient |  | 2050
260 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 1829.5788 | Ambient | Ambient | 2025 | 12 | Ambient | C | Ambient | Ambient |  | L
261 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 2703.7108 | Ambient | Ambient | 2975 | 18 | Ambient | C | Ambient | Ambient |  | 6400
262 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 1365.4078 | Ambient | Ambient | 1525 | 10 | Ambient | C | Ambient | Ambient
263 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 772.4888 | Ambient | Ambient | 850 | 6 | Ambient | C | Ambient | Ambient
264 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 1473.8273 | Ambient | Ambient | 1625 | 10 | Ambient | C | Ambient | Ambient
265 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 813.1461 | Ambient | Ambient | 900 | 6 | Ambient | C | Ambient | Ambient |  | 6000
266 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 640.3526 | Ambient | Ambient | 725 | 6 | Ambient | C | Ambient | Ambient
267 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 579.3666 | Ambient | Ambient | 650 | 4 | Ambient | C | Ambient | Ambient
268 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 643.7407 | Ambient | Ambient | 725 | 6 | Ambient | C | Ambient | Ambient
269 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 857.1915 | Ambient | Ambient | 950 | 6 | Ambient | C | Ambient | Ambient
270 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 1043.5375 | Ambient | Ambient | 1150 | 8 | Ambient | C | Ambient | Ambient
271 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 1138.4046 | Ambient | Ambient | 1275 | 8 | Ambient | C | Ambient | Ambient
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 18012.8804 | 0 | 0 | 20000 | 130 | 0 |  | 0 | 0
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
272 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
273 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
274 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
275 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
276 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
277 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
278 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
279 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
280 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
281 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
282 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
283 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
284 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
285 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
286 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
287 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
288 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
289 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
290 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
291 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
292 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
293 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
294 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
295 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
296 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
297 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
298 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
299 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
300 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
301 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
302 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
303 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
304 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
305 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
306 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
307 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
308 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
309 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
310 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
311 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
312 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
313 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
314 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
315 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
316 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
317 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
318 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
319 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
320 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
321 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
322 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
#DIV/0! | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details
323 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size
324 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! | #DIV/0! | W | 150 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4 | #DIV/0! | #DIV/0! | 2 | #DIV/0!
325 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
326 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | H
327 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
328 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | L
329 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
330 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
331 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
332 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
333 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0! |  | #DIV/0!
334 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
335 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
336 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
337 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
338 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
339 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | C | 0 | #DIV/0!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!

## Output BOQ
Sub.: Offer for Class 100K AC & Ventilation System and NC System for your PB - C and Pilot Plan Reg.
S.No. | Description & Specifications | [5 empty] | Units | Qty | Supply |  | Installation
[9 empty] | Rate | Amount | Rate | Amount
I | AIR HANDLING UNITS
| Supply, Installation, Testing & Commissioning of Factory assembled/ modular Single / Double Skin floor mounted type Air Handling Units (AHUs)(Single / Double Decker as per Plant Room Specs. AHUs shall be complete with Single skin 25 mm panels with 1.2mm Zinc / G.I. Sheets or double skin 25/47 mm thick insulated panels with CFC free polyurethane foam (PUF) insulation material with minimum density of 42 Kg/m3, sandwiched between 0.63/0.8 mm thick Aluminium Zinc / G.I.Sheets (inner skin) and pre-coated G.I. Sheets (outer skin). The AHUs shall be complete with mixing box with necessary openings and provosion for aluminium dampers for teminating return air and fresh air ducts. Food grade self-adhesive coated EPDM gaskets shall be provided between panels and structure of the AHU to ensure the entire housing is airtight, and should meet clean room class leakage requirments as per Standards. The AHUs shall be complete with provision for Fresh air filter section/ pre-filter section/ fine-filter or filters section/Superfine filter sections as mentioned below along without/with cooling coil section with specified multirows deep chilled water cooling coil of copper tube & aluminium fin construction to be sized for Cooling load specified with all controls & accessories, Re-heat section complete with finned type strip heaters, SS drain pan constructed from 18 gauge stainless steel & factory insulated with closed cell elastomeric Class 'O' material, copper header with "Copper to MS" adopter for Evaporator coil made out of 1/2" / 5/8" copper tubes with MS Header/Distributor with 12-13 FPI of mentioned capacities., all adaptive controls such as airstat, geyserstat, safetystat complete with wiring & vibration isolation pads etc. and all complete as per the specifications for Air-conditioning. AHUs shall be selected for a maximum face velocity of 500 FPM (2.5 MPS) and as per the Schedule of Air Handling Units. fan section with backward curved centrifugal fan (Kruger / Nicotra / Equivalent Make) with V-Belt drive arrangement and access doors where ever necessary with Motor (Crompton / equivalent Make) and Fan outlet velocity shall not exceed as per selected blower ratings and not more than 2000 FPM (10.2 MPS). AHUs should have marine lamps including adequately rated LED inside the AHU Cabinets. AHU inspection doors should have view windows with perfectly sealed gaksets on either side to ensure air tightness. All AHU doors shall be provided with door limit switch and door safety GI guard as well. | [34 empty] | Gear Type Aluminium Volume Control Dampers | Fire Retardent / Control Dampers
[30 empty] | Fresh Air |  |  |  |  | Exhaust
[30 empty] | 20 Micron | 10 Micron | 5 Micron | 1 Micron | 0.3 Micron | 20 Micron
AHU - 1 Air-Conditioning System (DX)
| CLASS | Class100K | CFM | 15750 | AC Load | 56 | Nos. | 1 | 867500 | 867500 |  |  |  | 867500 | 625 | 410140.9375 | 235200 | 15000 | 77950 | 129150 | 710 | 710 | 0 | 15000 | 6 | 6 | 36 | 150 | 6000 | 0 | 36 | 36 | 36 | 0 | FALSE | 31.5 | 14.3182
| AHU(W) | 2050 | AHU(H) | 2050 | AHU(L) | 5900
| Blower | 710 | Static Pr | 125 | Motor Hp | 20
| Coil Rows | 8 | Coil Head Type | Distributor | Coil Size hxw in mm | 1293 h x 1650 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 6 | 6
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 610 | 150 | 9
| 5µ | 610 | 610 | 300 | 9
| 1µ | 610 | 610 | 300 | 9
| 0 | 0 | 0 | 0 | 0
| EXHAUST | AHU - 1 Air-Conditioning System (DX)
| No. of Filtr. Stages | 1 | CFM | 0 | Filter Ratings | 20µ | Nos. | 1 | 406750 | 406750
| AHU(W) | 2050 | AHU(H) | 2050 | AHU(L) | 2400
| Blower | 200 | Static Pr | 50 | Motor Hp | 1
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos | [8 empty] | 406750 | 375 | 130280.0625 | 235200 | 5000 | 17150 | 19050 | 200 | 0 | 0 | 10000 | 12 | 12 | 144 | 150 | 0 | 0 | 0 | FALSE | 0 | 0 | 0 | 0 | 0
|  | 6 | 6
| 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0
AHU - 2 Air-Conditioning System (DX)
| CLASS | ISO 6 | CFM | 48500 | AC Load | 124.5 | Nos. | 1 | 1911500 | 1911500 |  |  |  | 1911500 | 625 | 883396 | 522900 | 25000 | 0 | 480000 | 1200 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 10500 | 0 | 36 | 36 | 36 | 0 |  | 97 | 44.0909
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1200 | Static Pr | 150 | Motor Hp | 75
| Coil Rows | 4 | Coil Head Type | Distributor | Coil Size hxw in mm | 2635 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 4 Air-Conditioning System (Chilled Water)
| CLASS | GRADE A | CFM | 47000 | AC Load | 159 | Nos. | 1 | 2179000 | 2179000 |  |  |  | 2179000 | 625 | 1006060 | 667800 | 25000 | 0 | 480000 | 1200 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 10300 | 0 | 36 | 36 | 36 | 36 |  | 94 | 42.7273
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 7000
| Blower | 1200 | Static Pr | 150 | Motor Hp | 75
| Coil Rows | 6 | Coil Head Type | Header | Coil Size hxw in mm | 2244 h x 3600 w
| No. of Filtr. Stages | 4 | Filter Ratings | 10µ, 5µ, 1µ & 0.3µ (HEPA Plenum Fitted 95% eff.)
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0.3µ 95% Eff. HEPA Filetr | 610 | 915 | 300 | 6
AHU - 5 Air-Conditioning System (DX)
| CLASS | 10K | CFM | 36500 | AC Load | 94 | Nos. | 1 | 1784750 | 1784750 |  |  |  | 1784750 | 625 | 717692 | 394800 | 20000 | 286500 | 365580 | 1120 | 0 | 0 | 20000 | 10 | 8 | 80 | 150 | 9100 | 0 | 36 | 36 | 36 | 0 |  | 73 | 33.1818
| AHU(W) | 3600 | AHU(H) | 2900 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 50
| Coil Rows | 4 | Coil Head Type | Distributor | Coil Size hxw in mm | 2238 h x 3200 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 10 | 8
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 6 Air-Conditioning System (Chilled Water)
| CLASS | NC | CFM | 27500 | AC Load | 74.5 | Nos. | 1 | 1414750 | 1414750 |  |  |  | 1414750 | 625 | 622129.75 | 312900 | 20000 | 178900 | 280680 | 1000 | 1000 | 0 | 20000 | 8 | 8 | 64 | 150 | 7900 | 0 | 36 | 36 | 36 | 0 |  | 55 | 25
| AHU(W) | 2900 | AHU(H) | 2900 | AHU(L) | 5800
| Blower | 1000 | Static Pr | 150 | Motor Hp | 40
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2271 h x 2500 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 8 | 8
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 7 Air-Conditioning System (Chilled Water)
| CLASS | 5 Micron | CFM | 28250 | AC Load | 98 | Nos. | 1 | 1529000 | 1529000 |  |  |  | 1529000 | 625 | 637731.75 | 411600 | 20000 | 178900 | 280680 | 1000 | 1000 | 0 | 20000 | 8 | 8 | 64 | 150 | 8000 | 0 | 36 | 36 | 36 | 0 |  | 56.5 | 25.6818
| AHU(W) | 2900 | AHU(H) | 2900 | AHU(L) | 6000
| Blower | 1000 | Static Pr | 150 | Motor Hp | 40
| Coil Rows | 6 | Coil Head Type | Header | Coil Size hxw in mm | 1991 h x 2500 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 8 | 8
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 8 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 9 Air-Conditioning System (DX)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 159 | Nos. | 1 | 2282750 | 2282750 |  |  |  | 2282750 | 625 | 883396 | 667800 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Distributor | Coil Size hxw in mm | 3366 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 10 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 11 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 12 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 13 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 14 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 15 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 15 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 16 Ventilation System ( SUPPLY )
| CLASS | ISO 6 | CFM | 20000 | AC Load | 0 | Nos. | 1 | 749500 | 749500 |  |  |  | 749500 | 375 | 401361.45 | 0 | 20000 | 119650 | 208320 | 800 | 800 | 0 | 20000 | 8 | 8 | 64 | 150 | 6800 | 36 | 36 | 36 | 36 | 0 |  | 40 | 18.1818
| AHU(W) | 2900 | AHU(H) | 2900 | AHU(L) | 6400
| Blower | 800 | Static Pr | 150 | Motor Hp | 30
| Coil Rows | Amb | Coil Head Type | Amb | Coil Size hxw in mm | 0
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 8 | 8
| 20µ | 610 | 915 | 100 | 6
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 19 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 20 Air-Conditioning System (Chilled Water)
| CLASS | ISO 5 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2173000 | 2173000 |  |  |  | 2173000 | 625 | 985616 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 36 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 6800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 4 | Filter Ratings | 10µ, 5µ, 1µ & 0.3µ (HEPA Plenum Fitted 95% eff.)
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0.3µ 95% Eff. HEPA Filetr | 610 | 915 | 300 | 6
AHU - 21 Air-Conditioning System (Chilled Water)
| CLASS | ISO 7 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
B | NC Areas. ( 5 MICRON AC SUPPLY) ( PBC Block)
Double Skin AHU made out of Al. Hollow Section and 24 G GI Panels 25 mm thick duly filled with PUF with provision for Filter sections of 20 micron Fresh air, 10 micron Prefilter , 5 micron fine filtration, 1 micron Superfine Filtration, and 0.3 micron 95% HEPA Filter Section , fan section with backward curved centrifugal fan of 110 mm static pressure (Kruger Make) with V-Belt drive arrangement and access doors where ever necessary with FLP Motor (Crompton Make) of following capacities.
| Width | Height | Length | Cfm | Blower length | Filtrat. Length | [7 empty] | 679400
VSU - 001 | 1750 | 1550 | 7100 | 9000 | 1800 | 3800 | Nos. | 1 | 491400 | 491400 | 54600 | 54600 | 546000 | 546000 | 625 | 369858.1875 | 0 | 10000 | 45650 | 120420 | 560 | 560 | 0 | 10000 | 5 | 4 | 20 | 150 | 4500 | 20 | 20 | 20 | 20 | 20 |  | 18 | 8.1818
| 560 | 12.5 | 0 | 1200 | 5 | 0
| BDB | Motor | TR | Coil Depth | Filtrat. Stages | Coil Rows | [7 empty] | 0
C | NC Areas. ( 5 MICRON AC SUPPLY)
Double Skin AHU made out of Al. Hollow Section and 24 G GI Panels 25 mm thick duly filled with PUF with provision for Filter sections of 20 micron Fresh air, 10 micron Prefilter , 5 micron fine filtration, fan section with backward curved centrifugal fan of 90 mm static pressure (Kruger Make) with V-Belt drive arrangement and access doors where ever necessary with FLP Motor (Crompton Make) of following capacities.
PBC Block
| Width | Height | Length | Cfm | Blower length | Filtrat. Length
FAM - 001 | 950 | 950 | 5400 | 1850 | 1600 | 2300 | Nos. | 1 | 185625 | 185625 | 20625 | 20625 | 206250 | 206250 | 625 | 156204.9375 | 0 | 5000 | 18900 | 26100 | 250 | 450 | 250 | 5000 | 2 | 2 | 4 | 150 | 2100 | 4 | 4 | 4 | 4 |  |  | 3.7 | 1.6818
| 250 | 1.5 | 0 | 1200 | 3 | 0
FAM - 002 | 950 | 950 | 5400 | 1950 | 1600 | 2300 | Nos. | 1 | 185625 | 185625 | 20625 | 20625 | 206250 | 206250 | 625 | 156204.9375 | 0 | 5000 | 18900 | 26100 | 250 | 450 | 250 | 5000 | 2 | 2 | 4 | 150 | 2100 | 4 | 4 | 4 | 4 |  |  | 3.9 | 1.7727
| 250 | 1.5 | 0 | 1200 | 3 | 0
| BDB | Motor | TR | Coil Depth | Filtrat. Stages | Coil Rows | [7 empty] | 453500
VSU - 002 | 1550 | 1100 | 5450 | 3900 | 1650 | 2300 | Nos. | 1 | 273825 | 273825 | 30425 | 30425 | 304250 | 304250 | 625 | 228650 | 0 | 8000 | 21900 | 45600 | 355 | 450 | 355 | 8000 | 4 | 2 | 8 | 150 | 3000 | 8 | 8 | 8 | 8 |  |  | 7.8 | 3.5455
| 355 | 5 | 0 | 1200 | 3 | 0
VSU - 003 | 1550 | 1250 | 5450 | 4450 | 1650 | 2300 | Nos. | 1 | 290250 | 290250 | 32250 | 32250 | 322500 | 322500 | 625 | 244336.0625 | 0 | 8000 | 24400 | 45600 | 400 | 450 | 400 | 8000 | 4 | 3 | 12 | 150 | 3200 | 12 | 12 | 12 | 12 |  |  | 8.9 | 4.0455
| 400 | 5 | 0 | 1200 | 3 | 0
PP Block
VSU - 004 | 1750 | 1550 | 5600 | 9000 | 1800 | 2300 | Nos. | 2 | 364275 | 728550 | 40475 | 80950 | 404750 | 404750 | 625 | 303280.6875 | 0 | 10000 | 45650 | 45600 | 560 | 560 | 0 | 10000 | 5 | 4 | 20 | 150 | 9000 | 20 | 20 | 20 | 20 |  |  | 18 | 8.1818
| 560 | 5 | 0 | 1200 | 3 | 0
VSU - 005 | 1750 | 1550 | 5600 | 10000 | 1800 | 2300 | Nos. | 2 | 364275 | 728550 | 40475 | 80950 | 404750 | 404750 | 625 | 303280.6875 | 0 | 10000 | 45650 | 45600 | 560 | 560 | 0 | 10000 | 5 | 4 | 20 | 150 | 9500 | 20 | 20 | 20 | 20 |  |  | 20 | 9.0909
| 560 | 5 | 0 | 1200 | 3 | 0
D | EXHAUST SYSTEM ( VENTILATION )
Single Skin AHU made out of Al. Hollow Section and 18 G GI Panels 25 mm thick with provision for Filter sections of 20 Micron exhaust air, fan section with backward curved centrifugal fan of 50 mm static pressure (Kruger Make) with V-Belt drive arrangement and access doors where ever necessary with FLP Motor (Crompton Make).
PBC Block
| Width | Height | Length | Cfm | Blower length | Filtrat. Length
FEM - 001 | 950 | 950 | 2100 | 1750 | 1600 | 500 | Nos. | 1 | 91575 | 91575 | 10175 | 10175 | 101750 | 101750 | 450 | 51748.875 | 0 | 5000 | 18900 | 26100 | 250 | 450 | 250 | 5000 | 2 | 2 | 4 | 150 | 2000 | [5 empty] | 4 | 2.6923 | 1.5909
| 250 | 1.5 | 0 | 0 | 1 | 0
FEM - 002 | 950 | 950 | 2100 | 1825 | 1600 | 500 | Nos. | 1 | 91575 | 91575 | 10175 | 10175 | 101750 | 101750 | 450 | 51748.875 | 0 | 5000 | 18900 | 26100 | 250 | 450 | 250 | 5000 | 2 | 2 | 4 | 150 | 2100 | [5 empty] | 4 | 2.8077 | 1.6591
| 250 | 1.5 | 0 | 0 | 1 | 0
| BDB | Motor | TR | Coil Depth | Filtrat. Stages | Coil Rows
VEU - 001 | 1750 | 1550 | 2300 | 8575 | 1800 | 500 | Nos. | 1 | 192825 | 192825 | 21425 | 21425 | 214250 | 214250 | 450 | 112903.335 | 0 | 10000 | 45650 | 45600 | 560 | 560 | 0 | 10000 | 5 | 4 | 20 | 150 | 4400 | [5 empty] | 20 | 13.1923 | 7.7955
| 560 | 5 | 0 | 0 | 1 | 0
VEU - 002 | 1550 | 1100 | 2150 | 3700 | 1650 | 500 | Nos. | 1 | 131400 | 131400 | 14600 | 14600 | 146000 | 146000 | 450 | 79941.42 | 0 | 8000 | 21900 | 36000 | 355 | 450 | 355 | 8000 | 4 | 2 | 8 | 150 | 2900 | [5 empty] | 8 | 5.6923 | 3.3636
| 355 | 3 | 0 | 0 | 1 | 0
VEU - 003 | 1550 | 1250 | 2150 | 4200 | 1650 | 500 | Nos. | 1 | 137250 | 137250 | 15250 | 15250 | 152500 | 152500 | 450 | 86441.805 | 0 | 8000 | 21900 | 36000 | 355 | 450 | 355 | 8000 | 4 | 3 | 12 | 150 | 3100 | [5 empty] | 12 | 6.4615 | 3.8182
| 355 | 3 | 0 | 0 | 1 | 0
| BDB | Motor | TR | Coil Depth | Filtrat. Stages | Coil Rows
PP Block
VEU - 004 | 1750 | 1550 | 2200 | 8250 | 1700 | 500 | Nos. | 2 | 182700 | 365400 | 20300 | 40600 | 203000 | 203000 | 450 | 109707.615 | 0 | 10000 | 37450 | 45600 | 500 | 500 | 0 | 10000 | 5 | 4 | 20 | 150 | 8700 | [5 empty] | 20 | 12.6923 | 7.5
| 500 | 5 | 0 | 0 | 1 | 0
VEU - 005 | 1750 | 1550 | 2300 | 9250 | 1800 | 500 | Nos. | 2 | 192825 | 385650 | 21425 | 42850 | 214250 | 214250 | 450 | 112903.335 | 0 | 10000 | 45650 | 45600 | 560 | 560 | 0 | 10000 | 5 | 4 | 20 | 150 | 9200 | [5 empty] | 20 | 14.2308 | 8.4091
| 560 | 5 | 0 | 0 | 1 | 0
PBC Block
Ex. 1 Modules | 600 | 600 | 2100 | 575 | 1600 | 500 | Nos. | 4 | 64575 | 258300 | 7175 | 28700 | 71750 | 71750 | 450 | 29633.04 | 0 | 5000 | 17150 | 19920 | 200 | 450 | 200 | 5000 | 1 | 1 | 1 | 150 | 4600 | [5 empty] | 1 | 0.88462 | 0.52273
|  | 0.5 | 0 | 0 | 1 | 0
Ex. 2 Modules | 600 | 600 | 2100 | 300 | 1600 | 500 | Nos. | 1 | 64575 | 64575 | 7175 | 7175 | 71750 | 71750 | 450 | 29633.04 | 0 | 5000 | 17150 | 19920 | 200 | 450 | 200 | 5000 | 1 | 1 | 1 | 150 | 900 | [5 empty] | 1 | 0.46154 | 0.27273
|  | 0.5 | 0 | 0 | 1 | 0
PP Block
Ex. 2 Modules | 600 | 600 | 2100 | 300 | 1600 | 500 | Nos. | 2 | 64575 | 129150 | 7175 | 14350 | 71750 | 71750 | 450 | 29633.04 | 0 | 5000 | 17150 | 19920 | 200 | 450 | 200 | 5000 | 1 | 1 | 1 | 150 | 1700 | [5 empty] | 1 | 0.46154 | 0.27273
|  | 0.5 | 0 | 0 | 1 | 0
II | AIR CIRCULATION SYSTEM | [25 empty] | 2300 |  | 224100
Ducting Works
1 | 24 G GI ducting with MS angle joints duly with rubber | [5 empty] | Sft | 89000 | 116.2 | 10341800 | 11.62 | 1034180 | 116.2 | 116.2 | [15 empty] | 130 | 780 | 780 | 780 | 100 | 100 | 1580 | 730
gasket joined with GI plated 06 mm Nut bolts and
supported by 8 mm GI threaded rods and Sealed
duly with Silicon Sealant on joints
2 | 22 G GI ducting with MS angle joints duly with rubber | [5 empty] | Sft | 78500 | 125.5 | 9851750 | 12.55 | 985175 | 125.5 | 125.5
gasket joined with GI plated 06 mm Nut bolts and
supported by 8 mm GI threaded rods and Sealed
duly with Silicon Sealant on joints
3 | 20 G GI ducting with MS angle joints duly with rubber | [5 empty] | Sft | 59500 | 134.8 | 8020600 | 13.48 | 802060 | 134.8 | 134.8 | [15 empty] | 20 micr | 10 micr | 5 micr | 1 micr | 0.3 micr | 20 micr Exhaust | Al Dampers | Al Dampers
gasket joined with GI plated 06 mm Nut bolts and
supported by 8 mm GI threaded rods and Sealed
duly with Silicon Sealant on joints
Insulation Works
4 | 13 mm thick Cross linked closedcell foil faced | [5 empty] | Sft | 112500 | 72 | 8100000 | 7.2 | 810000 | 72 | 72
insulation for return air with taped joints.
5 | 19 mm thick Cross linked closedcell foil faced | [5 empty] | Sft | 112500 | 80 | 9000000 | 8 | 900000 | 80 | 80
insulation for Supply air with taped joints.
Grills / Diffusers / Perforated
6 | SS 316. Perforated Grills duly boughed | [5 empty] | Sft | 10740 | 1100 | 11814000 | 110 | 1181400 | 1100 | 1100
for Supply & return air in 100K & NC areas
Fire Resistant / Retardant / Control Dampers
7 | Fire Resistant Opposite Blade type Volume control | [5 empty] | Sft | 730 | 1400 | 1022000 | 140 | 102200 | 1400 | 1400
dampers at AHU made out of 18 GI duly epoxy
powder coated / PU painted with fusible link.
Volume Control Dampers
7 | Opposite Blade type Volume control Dampers for Air | [5 empty] | Sft | 220 | 750 | 165000 | 75 | 16500 | 750 | 750
distribution control in ducts made out of 20 GI
duly Epoxy powder coated / PU painted.
8 | Gear type control Dampers for distribution | [5 empty] | Sft | 2310 | 1500 | 3465000 | 150 | 346500 | 1500 | 1500
AHU's for Supply , Fresh air , Retrun Air & Exhaust Air.
Terminal Filtration \ Grill Modules
9 | Supply, return & Exhaust Air filter Modules for | [5 empty] | Sft | 8936 | 2750 | 24574000 | 275 | 2457400 | 2750 | 2750
fixing Terminal Filters and grills duly epoxy powder coated made
out of 18/20 G CRCA for 100 K,5 & 20 micron
areas. with Gear Mechanism.
10 | Flexible canvas connections for AHU Inlets, Outlets, fresh air Terminal Grill | [5 empty] | Sft | 9850 | 150 | 1477500 | 15 | 147750 | 150 | 150
/Filter Modules , Terminals , Blowers, and plenum connections & others if any.
III | AIR FILTRATION SYSTEM
1 | 10 micron filters made out of HLP media with | [5 empty] | Sft | 780 | 550 | 429000 | 55 | 42900 | 550 | 550
one side HDPE & other side Al. expanded mesh of
efficiency 95% (150mm)
2 | 5 micron filters made out of SNPF media with | [5 empty] | Sft | 780 | 750 | 585000 | 75 | 58500 | 750 | 750
one side HDPE & other side Al. expanded mesh of
efficiency 99%(300 mm) ( 150 GSM )
3 | 1 micron filters made out of SNPF media with | [5 empty] | Sft | 780 | 850 | 663000 | 85 | 66300 | 850 | 850
one side HDPE & other side Al. expanded mesh of
efficiency 99.9%(300 mm)( 200 GSM )
4 | 20 micron filters made out of HDPE media with | [5 empty] | Sft | 130 | 500 | 65000 | 50 | 6500 | 500 | 500
one side HDPE & other side Al. expanded mesh of
efficiency 90%(150 mm) for fresh air supply
5 | 20 micron filters made out of HDPE media with | [5 empty] | Sft | 100 | 500 | 50000 | 50 | 5000 | 500 | 500
one side HDPE & other side Al. expanded mesh of
efficiency 90%(150 mm) for Exhaust air.
6 | 0.3 micron (HEPA) filters made out of | [5 empty] | Sft | 100 | 3250 | 325000 | 975 | 97500 | 3250 | 3250
imported lydall media of efficiency 95% for ISO 8 / 100K / ISO 5, 100 Areas.
7 | 10 micron filters made out of HLP media with | [5 empty] | Sft | 4500 | 400 | 1800000 | 40 | 180000 | 400 | 400
one side HDPE & other side Al. expanded mesh of
efficiency 95% (50mm thick)for Return air in Class
100K & 5 Micron Areas.
8 | 5 micron filters made out of SNPF media | [5 empty] | Sft | 4500 | 450 | 2025000 | 45 | 202500 | 450 | 450
with one side HDPE & other side Al. expanded mesh
of efficiency 95% (50mm thick) for Supply air in
Class 100K & 5 Micron Areas.
9 | 0.3 micron (HEPA) filters made out of imported lydall media of 300 mm Thick | [5 empty] | Sft | 350 | 3250 | 1137500 | 325 | 113750 | 450 | 3250
efficiency 99.95%/99.97%/99.997% for 10K or ISO 7 Area.
10 | 0.3 micron (HEPA) filters made out of imported lydall media of 150 mm Thick | [5 empty] | Sft | 3950 | 3250 | 12837500 | 325 | 1283750 | 450 | 3250
efficiency 99.995%/99.997% for 1K or Class 100 or ISO 6 or ISO 5 Area.
11 | 0.12 micron (ULPA) filters made out of imported lydall media of 65/80 mm Thick | [5 empty] | Sft | 950 | 3250 | 3087500 | 325 | 308750 | 450 | 3250
efficiency 99.9997% / 99.9999% for Class 100 / Class 10 / Class 1/ ISO 5 / ISO 4 / ISO 3 Area.
IV | PRESSURE MONITORING SYSTEM
1 | 0-10 mm DWYER make Magnehelic Guages | [5 empty] | Nos. | 320 | 6750 | 2160000 | 750 | 240000 | 7500 | 7500 | =COUNTIFS('BOD-Cold & Amb.'!istext(N10:N225)) | 176
for Room pressures indication
2 | 0-50 mm DWYER make Magnehelic Guages | [5 empty] | Nos. | 59 | 6750 | 398250 | 750 | 44250 | 7500 | 7500
for filter pressure drop indication in AHU's
3 | SS 304 Individual Magnehelic gauge housing | [5 empty] | Nos. | 379 | 3600 | 1364400 | 400 | 151600 | 4000 | 4000
| with sensor | [12 empty] | 4000
4 | SMART PROCESS SCANNERS with in built Sensor | [5 empty] | Nos. | 304 | 67500 | 20520000 | 7500 | 2280000 | 75000 | 75000
Make:POLMON
Specifications:
In built :RH,Temperature & DP
Output Type-Modbus
X-Future Use
Display: RH, TEMP. and DP
Set point for each parameter (Hi/Low).
Display Blinking on Violation (Optional Buzzer Indication).
Programmable Damping/ Filter constant for each parameter.
Independent Displays for each parameter.
Diagnostic messages for each parameter.
Fully Differential Inputs.
Optically Isolated communication port.
Programmable Baud Rate Selection 1200/ 9600/ 19.2KB/ 38.4KB.
Power Supply: 24 VAC
SS face plate
Mounting: Modular Wall Mounting
5 | DP TRANSMITTERS FOR CLEAN ROOMS | [5 empty] | Nos. | 304 | 45000 | 0 | 5000 | 0 | 50000 | 50000
Make:POLMON
Local Display:required
Specifications:
1-Face Plate Of Material- SS
X- 0-12mm WC
Lifetime Stability of -/+0.5% F.S.O
No Calibration or recalibration necessary for the life of the device
Standard 2-Year warranty
Accuracy:1% on FSO
Output:4-20mA
Calibrated to NIST-Traceable standards
Media compatability:clean,dry inert,non-ferrous gases
6 | DP MOUNTING BOX WITH ACCESSORIES | [5 empty] | Nos. | 304 | 2700 | 820800 | 300 | 91200 | 3000 | 3000
1-Type Of Material-SS-304
1-Depth-1-50mm
V | VALIDATION
1 | Commissioning & Validation of Total Clean Room | [5 empty] | L/s. | 1 | 0 | 0 | 600000 | 600000 | 600000 | 600000
| (Air Balancing,Temp., Pressure Balancing, Particle | [10 empty] | . |  | .
Count, HEPA Integrity Test (D.O.P), recovery Test
with DQ/IQ/OQ/PQ reports)
[10 empty] | 176837125 |  | 15081390
191918515
Terms & Conditions :
1 | The above prices are inclusive of Packing, Forwarding, erection & Commissioning of the system.
2 | Transportation Charges & Unloading Charges extra at actuals in client's scope.
3 | Accomodation at Site Shall be provided for 20 - 25 Persons at the cost of Client.
4 | GST@18% extra
7 | However any tax variations at the time of delivery shall be applicable as per actuals.
8 | All civil, False Ceiling works & electrical cabling, starters, Panel Boards etc. will be in client's scope.
9 | All electrical cable connections shall be connected to AHU motors at the installated Areas.
10 | Ducting, Dampers, Insulation,Grills & terminal modules with Filters are tentative and will be charged as per actuals.
11 | Scaffoldings or support structures required if any shall be in clients scope
12 | All heat loads are based on calculations as per oral references, if any changes as per practical site conditions
shall be reworked along with prices.
13 | All test Certificates along with Calibration & Traceable certificates will be provided.
14 | All detailed equipment / duct drawings will be submitted for approvals against your W.O. / LOI along with Advance.
15 | Chilled water/ DX connections along with all piping & controls with accessories does not include in our scope.
Along with Condensing Units / Chiller Plant.
16 | Dehumidifier is necessary to control humidity anything below 55+/-5% along with prec-cooling of fresh Air.
17 | Drain water connections along with all piping & accessories does not include in our scope.
18 | All equipments are guaranteed against any manufacturing defects for a period of 12 months from the date of
Commissioning or 15 months from the date of supply which ever is earliest.
18 | DELIVERY: 06-08 months from the date of Confirmed P.O. & ADVANCE
( From the date of approval of Layout Drawings, Duct routing Drawings, AHU's drawings etc.)
Installation within 10 months, Commissioning - 1 month, Documentation ( DQ/IQ/OQ/PQ) - 1 month
19 | Payment : Supply : 50 % advance, 50 % against Proforma Invoice on Pro-rata Basis. Installation : 50% Advance,
balance against installation & commissioning.
20 | If Canteen facilities can be provided at your site work for 20-25 Persons to complete the work at a faster rate shall be helpful..
21 | Safe Working Place and material Storage place for & from our ---------------company shall be provided at Site at clients cost.
22 | Lifting, Shifting, Positioning of all Heavy and necessary material at site is in Client's Scope.
23 | Offer Validity : 15 days.
we hope the above will meet your requirement and please feel free to contact us for any Techno-commercial
discussions in this regard.

## BOD-Cold & Amb.
VLOOKUP(A30,$C$35:$F$254,4,FALSE)
Zoning Area AHU - 1 Air-Conditioning System (DX) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
S.No. | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
1 | Chandrashekar | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 | 15750 | W | 125 | 710 | 20 | 8 | 56 | 3 | 224 | 14.1322 | 2 | 94.8756 |  |  |  |  | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
2 | vijay bhasker | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 |  | 2050 | [14 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
3 | nimma | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 |  | H | [14 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
4 | sahajanand | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 |  | 2050 | [14 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
5 | xyz | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 |  | L | [14 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
6 | abc | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 |  | 5900 | [14 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
7 | excel | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 | [16 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
8 | word | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 | [16 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
9 | java | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 | [16 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
10 | 12345 | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 |  | 5500 | [14 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
11 | cvdwvjvq | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 | [16 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
12 | jcvbbvk | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 | [16 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
13 | vbwbvb | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 | [16 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
14 | b cjvjvve | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 | [16 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
15 | ifhiuhfigi | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 | [16 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
16 | hbhwbfb | 1 | 1 | 2 | 1 | 2 | 1.75 | 2 | 10% | 0% | 24 | 50 | 41 | 85 | Class100K | 12 | 0 | 100 | Class100K | 12 | 10.76 | 70.5856 | 14.1171 | 1.4117 | 0 | 0.098308 | 975 | 975 | 0 | 3.5 | D | 2.5 | 3.5 | [16 empty] | 14.4 | 30.6 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 41 | 85 | 303.877 | 24 | 50 | 65.0626 | 238.8144 | 1185.3216 | 557.7984 | 69.7248 | 148.1652 | 9418.68 | 6824 | 64.248 | 11664 | 46.6543 |  | 32478.7572 | 121795.3394 | 229.2533 | 2063.2793 | 29202.9038 | 156566.6292 | 185769.533 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -1673.3952 | -1673.3952 | 69.7248 | -209.1744 | -13296.96 | 6824 | 64.248 | 11664 | -65.8648 |  | -5257.471 | -19715.5161 | -37.1102 | 55.3472 | 3376.5783 | -24954.7501 | -21578.1718
[21 empty] | 172.16 | 1129.3696 | 225.8739 | 22.5874 | 0 | 1.5729 | 15600 | 15600 | 0 | 56 |  | 40 | 56
Zoning Area AHU - 2 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
| Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
18 | Clean Room 10 | 3 | 3 | 2 | 1 | 2 | 1.75 | 3 | 15% | 10% | 24 | 50 | 43.1 | 100 | ISO 6 | 180 | -16.6 | 8 | ISO 6 | 180 | 96.84 | 635.2704 | 1905.8112 | 285.8717 | 190.5811 | 28.5967 | 3425 | 3425 | 20 | 9 | C | 5 | 9 | 48500 | W | 150 | 1200 | 75 | 4 | 124.5 | 3 | 498 | 31.4188 | 2 | 141.4637 |  |  |  |  | 14.4 | 34.38 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 43.1 | 100 | 408.118 | 24 | 50 | 65.0626 | 343.0554 | 3995.231 | 1673.3952 | 627.5232 | 1498.2116 | 10582.164 | 6824 | 578.2316 | 17496 | 17690.883 |  | 46655.5281 | 262437.3458 | 111145.7851 | 377895.6693 | 57166.5097 | 798134.3284 | 855300.8381 | 14.4 | -73.08 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | -16.6 | 8 | 0.57291 | 24 | 50 | 65.0626 | -64.4897 | -8492.4806 | -8492.4806 | 627.5232 | -3184.6802 | -22494.024 | 6824 | 578.2316 | 17496 | -37604.7043 |  | -8770.6038 | -49334.6462 | -20893.8936 | 7056.7618 | -46250.1343 | -71942.3818 | -118192.5162
19 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 42.6096 | 335.4228 | 894.4607 | 89.4461 | 0 | 8.2283 | 2425 | 2425 | 14 | 6.5 | C | 4.5 | 6.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 3651.5465 |  | 85810.1664 | 241341.093 | 19188.4559 | 172696.1029 | 51597.7783 | 519035.8182 | 570633.5965 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -4173.196 |  | -10514.9419 | -29573.2742 | -2351.3006 | 3506.7955 | -14173.0629 | -38932.7213 | -53105.7842
20 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 45.192 | 355.7514 | 948.6705 | 94.867 | 0 | 8.727 | 2475 | 2475 | 16 | 6.5 | C | 5 | 6.5 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 3872.8523 |  | 85810.1664 | 241341.093 | 20351.3926 | 183162.5334 | 58922.0634 | 530665.1854 | 589587.2488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -4426.1169 |  | -10514.9419 | -29573.2742 | -2493.8037 | 3719.3286 | -7921.2434 | -38862.6913 | -46783.9347
21 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 79.086 | 622.565 | 1660.1733 | 166.0173 | 0 | 15.2723 | 2800 | 2800 | 16 | 7 | C | 3 | 7 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 6777.4915 |  | 0 | 241341.093 | 35614.937 | 320534.4334 | 33077.4959 | 597490.4635 | 630567.9594 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -7745.7046 |  | 0 | -29573.2742 | -4364.1565 | 6508.825 | 6986.9555 | -27428.6057 | -20441.6502
22 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 116.208 | 914.7894 | 2439.4383 | 243.9438 | 0 | 22.4409 | 3975 | 3975 | 24 | 10 | C | 5.5 | 10 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 9958.7631 |  | 85810.1664 | 241341.093 | 52332.1524 | 470989.3715 | 60716.4886 | 850472.7834 | 911189.272 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -11381.4435 |  | -10514.9419 | -29573.2742 | -6412.6381 | 9563.9877 | -24606.5899 | -36936.8665 | -61543.4564
23 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 171.7296 | 1351.8554 | 3604.9478 | 360.4948 | 0 | 33.1627 | 5350 | 5350 | 32 | 13.5 | C | 7.5 | 13.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 14716.8387 |  | 128715.2496 | 241341.093 | 77335.2919 | 696017.6268 | 85407.016 | 1143409.2614 | 1228816.2774 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -16819.2443 |  | -15772.4129 | -29573.2742 | -9476.4541 | 14133.4486 | -38210.6394 | -40688.6927 | -78899.3321
24 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 86.7256 | 682.7039 | 1820.5438 | 182.0544 | 0 | 16.7476 | 3350 | 3350 | 20 | 8.5 | C | 5 | 8.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 7432.188 |  | 85810.1664 | 241341.093 | 39055.2915 | 351497.6236 | 57135.3417 | 717704.1746 | 774839.5162 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -8493.9291 |  | -10514.9419 | -29573.2742 | -4785.7281 | 7137.5686 | -20508.9859 | -37736.3756 | -58245.3615
25 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 49.0656 | 386.2444 | 1029.9851 | 102.9985 | 0 | 9.475 | 2775 | 2775 | 16 | 7 | C | 6 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 4204.8111 |  | 128715.2496 | 241341.093 | 22095.7977 | 198862.1791 | 67499.9914 | 591014.3194 | 658514.3109 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -4805.4984 |  | -15772.4129 | -29573.2742 | -2707.5583 | 4038.1282 | -25036.6575 | -44015.1173 | -69051.7747
26 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 93.612 | 736.9137 | 1965.1031 | 196.5103 | 0 | 18.0774 | 3500 | 3500 | 20 | 9 | C | 5 | 9 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 8022.3369 |  | 85810.1664 | 241341.093 | 42156.4561 | 379408.1049 | 57942.3158 | 748715.8204 | 806658.1362 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -9168.385 |  | -10514.9419 | -29573.2742 | -5165.7363 | 7704.3235 | -21432.3783 | -37549.6289 | -58982.0073
27 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 51.648 | 406.5731 | 1084.1948 | 108.4195 | 0 | 9.9737 | 2625 | 2625 | 16 | 7 | C | 4.5 | 7 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 4426.1169 |  | 85810.1664 | 241341.093 | 23258.7344 | 209328.6096 | 52777.73 | 559738.6034 | 612516.3335 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -5058.4193 |  | -10514.9419 | -29573.2742 | -2850.0614 | 4250.6612 | -15523.0705 | -38687.6163 | -54210.6868
28 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 40.6728 | 320.1763 | 853.8034 | 85.3803 | 0 | 7.8543 | 2400 | 2400 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 3485.5671 |  | 85810.1664 | 241341.093 | 18316.2533 | 164846.28 | 51332.381 | 510313.7928 | 561646.1739 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -3983.5052 |  | -10514.9419 | -29573.2742 | -2244.4233 | 3347.3957 | -13869.4322 | -38985.2438 | -52854.676
29 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 36.7992 | 289.6833 | 772.4888 | 77.2489 | 0 | 7.1063 | 2300 | 2300 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 3153.6083 |  | 85810.1664 | 241341.093 | 16571.8483 | 149146.6343 | 50801.5865 | 492869.742 | 543671.3285 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -3604.1238 |  | -10514.9419 | -29573.2742 | -2030.6687 | 3028.5961 | -13262.1707 | -39090.2888 | -52352.4595
30 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 40.888 | 321.8703 | 858.3209 | 85.8321 | 0 | 7.8959 | 2400 | 2400 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 3504.0092 |  | 85810.1664 | 241341.093 | 18413.1647 | 165718.4826 | 51352.1081 | 511282.9068 | 562635.0149 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -4004.582 |  | -10514.9419 | -29573.2742 | -2256.2986 | 3365.1068 | -13892.013 | -38979.4079 | -52871.4209
31 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 54.4456 | 428.5958 | 1142.922 | 114.2922 | 0 | 10.514 | 2675 | 2675 | 16 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 4665.8649 |  | 85810.1664 | 241341.093 | 24518.5825 | 220667.2426 | 53122.0358 | 572337.0846 | 625459.1203 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -5332.417 |  | -10514.9419 | -29573.2742 | -3004.4397 | 4480.9054 | -15917.0244 | -38611.7505 | -54528.7749
32 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 66.2816 | 521.7688 | 1391.3833 | 139.1383 | 0 | 12.7996 | 2925 | 2925 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 5680.1834 |  | 85810.1664 | 241341.093 | 29848.7091 | 268638.3823 | 54646.2932 | 625638.3509 | 680284.6441 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -6491.6381 |  | -10514.9419 | -29573.2742 | -3657.5788 | 5455.0152 | -17660.9858 | -38290.7797 | -55951.7655
33 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 160 | 0 | 100 | ISO 6 | 160 | 72.3072 | 569.2023 | 1517.8727 | 151.7873 | 0 | 13.9632 | 3050 | 3050 | 18 | 8 | C | 5 | 8 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 6196.5637 |  | 85810.1664 | 241341.093 | 32562.2282 | 293060.0534 | 55374.3589 | 652773.541 | 708147.8999 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -7081.7871 |  | -10514.9419 | -29573.2742 | -3990.0859 | 5950.9257 | -18494.0551 | -38127.3764 | -56621.4315
[21 empty] | 1144.1108 | 8879.3861 | 23890.1198 | 2484.3025 | 190.5811 | 230.835 | 48450 | 48450 | 288 | 124.5 |  | 79 | 124.5
Zoning Area AHU - 3 Air-Conditioning System (DX) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
34 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
35 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 96.84 | 762.3245 | 1905.8112 | 190.5811 | 0 | 17.532 | 3250 | 3250 | 34 | 11 | D | 4.5 | 11 | 47000 | W | 150 | 1200 | 75 | 6 | 159 | 4 | 636 | 40.1252 | 2 | 159.8671 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 7780.2836 |  | 42905.0832 | 241341.093 | 40884.4941 | 367960.4465 | 49584.5502 | 693091.1168 | 742675.667 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -8891.7527 |  | -5257.471 | -29573.2742 | -5009.8735 | 7471.8654 | -4569.7502 | -32368.7533 | -36938.5035
36 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 42.6096 | 335.4228 | 838.5569 | 83.8557 | 0 | 7.7141 | 2375 | 2375 | 24 | 8 | D | 4.5 | 8 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 3423.3248 |  | 85810.1664 | 241341.093 | 17989.1774 | 161902.5965 | 51369.5566 | 507043.0333 | 558412.59 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3912.3712 |  | -10514.9419 | -29573.2742 | -2204.3444 | 3287.6208 | -13912.2382 | -39004.9397 | -52917.1779
37 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 45.192 | 355.7514 | 889.3786 | 88.9379 | 0 | 8.1816 | 2425 | 2425 | 26 | 8.5 | D | 5 | 8.5 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 3630.799 |  | 85810.1664 | 241341.093 | 19079.4306 | 171714.875 | 58680.0101 | 517945.5651 | 576625.5752 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -4149.4846 |  | -10514.9419 | -29573.2742 | -2337.941 | 3486.8705 | -7644.6111 | -38939.2866 | -46583.8977
38 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 79.086 | 622.565 | 1556.4125 | 155.6412 | 0 | 14.3178 | 2700 | 2700 | 28 | 9 | D | 3 | 9 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 6353.8983 |  | 0 | 241341.093 | 33389.0035 | 300501.0313 | 32653.9027 | 575231.1279 | 607885.0306 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -7261.5981 |  | 0 | -29573.2742 | -4091.3967 | 6102.0234 | 7471.062 | -27562.6475 | -20091.5855
39 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 116.208 | 914.7894 | 2286.9734 | 228.6973 | 0 | 21.0384 | 3825 | 3825 | 40 | 13 | D | 5.5 | 13 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 9336.3404 |  | 85810.1664 | 241341.093 | 49061.3929 | 441552.5358 | 60094.066 | 817765.1882 | 877859.2541 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -10670.1033 |  | -10514.9419 | -29573.2742 | -6011.8482 | 8966.2385 | -23895.2497 | -37133.8259 | -61029.0756
40 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 171.7296 | 1351.8554 | 3379.6385 | 337.9639 | 0 | 31.09 | 5125 | 5125 | 52 | 17.5 | D | 7.5 | 17.5 |  | 7000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 13797.0363 |  | 128715.2496 | 241341.093 | 72501.8361 | 652516.5252 | 84487.2136 | 1095074.704 | 1179561.9176 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -15768.0415 |  | -15772.4129 | -29573.2742 | -8884.1757 | 13250.108 | -37159.4367 | -40979.7548 | -78139.1915
41 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 86.7256 | 682.7039 | 1706.7598 | 170.676 | 0 | 15.7008 | 3250 | 3250 | 34 | 11 | D | 5 | 11 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 6967.6762 |  | 85810.1664 | 241341.093 | 36614.3358 | 329529.0221 | 56670.8299 | 693294.6174 | 749965.4473 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -7963.0586 |  | -10514.9419 | -29573.2742 | -4486.6201 | 6691.4706 | -19978.1154 | -37883.3656 | -57861.481
42 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 49.0656 | 386.2444 | 965.611 | 96.5611 | 0 | 8.8829 | 2700 | 2700 | 28 | 9 | D | 6 | 9 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3942.0104 |  | 128715.2496 | 241341.093 | 20714.8103 | 186433.2929 | 67237.1907 | 577204.4459 | 644441.6366 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -4505.1547 |  | -15772.4129 | -29573.2742 | -2538.3359 | 3785.7452 | -24736.3138 | -44098.2779 | -68834.5917
43 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 93.612 | 736.9137 | 1842.2842 | 184.2284 | 0 | 16.9476 | 3375 | 3375 | 34 | 11.5 | D | 5 | 11.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 7520.9409 |  | 85810.1664 | 241341.093 | 39521.6776 | 355695.0983 | 57440.9197 | 722368.0354 | 779808.9551 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -8595.361 |  | -10514.9419 | -29573.2742 | -4842.8777 | 7222.8032 | -20859.3543 | -37708.2906 | -58567.6449
44 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 51.648 | 406.5731 | 1016.4326 | 101.6433 | 0 | 9.3504 | 2550 | 2550 | 26 | 8.5 | D | 4.5 | 8.5 |  | 6600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 4149.4846 |  | 85810.1664 | 241341.093 | 21805.0635 | 196245.5715 | 52501.0977 | 545201.8944 | 597702.9922 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -4742.2681 |  | -10514.9419 | -29573.2742 | -2671.9325 | 3984.9949 | -15206.9193 | -38775.1538 | -53982.0731
45 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 40.6728 | 320.1763 | 800.4407 | 80.0441 | 0 | 7.3634 | 2350 | 2350 | 24 | 8 | D | 4.5 | 8 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 3267.7191 |  | 85810.1664 | 241341.093 | 17171.4875 | 154543.3875 | 51114.5331 | 498866.1345 | 549980.6676 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -3734.5361 |  | -10514.9419 | -29573.2742 | -2104.1469 | 3138.1835 | -13620.4631 | -39054.1795 | -52674.6427
46 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 36.7992 | 289.6833 | 724.2083 | 72.4208 | 0 | 6.6621 | 2250 | 2250 | 24 | 7.5 | D | 4.5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2956.5078 |  | 85810.1664 | 241341.093 | 15536.1077 | 139824.9697 | 50604.486 | 482512.3369 | 533116.8229 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -3378.866 |  | -10514.9419 | -29573.2742 | -1903.7519 | 2839.3089 | -13036.913 | -39152.6592 | -52189.5722
47 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 40.888 | 321.8703 | 804.6758 | 80.4676 | 0 | 7.4024 | 2350 | 2350 | 24 | 8 | D | 4.5 | 8 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 3285.0086 |  | 85810.1664 | 241341.093 | 17262.3419 | 155361.0774 | 51133.1076 | 499774.6788 | 550907.7864 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3754.2956 |  | -10514.9419 | -29573.2742 | -2115.2799 | 3154.7876 | -13641.7266 | -39048.7085 | -52690.4351
48 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 54.4456 | 428.5958 | 1071.4894 | 107.1489 | 0 | 9.8569 | 2600 | 2600 | 26 | 9 | D | 4.5 | 9 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 4374.2484 |  | 85810.1664 | 241341.093 | 22986.1711 | 206875.5399 | 52830.4192 | 557012.9705 | 609843.3897 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -4999.141 |  | -10514.9419 | -29573.2742 | -2816.6622 | 4200.8488 | -15583.7483 | -38704.0296 | -54287.7779
49 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 66.2816 | 521.7688 | 1304.4219 | 130.4422 | 0 | 11.9997 | 2850 | 2850 | 30 | 9.5 | D | 5 | 9.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 5325.1719 |  | 85810.1664 | 241341.093 | 27983.1648 | 251848.4834 | 54291.2817 | 606982.9077 | 661274.1894 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -6085.9108 |  | -10514.9419 | -29573.2742 | -3428.9801 | 5114.0768 | -17255.2585 | -38403.1195 | -55658.3779
50 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | GRADE A | 150 | 0 | 100 | GRADE A | 150 | 72.3072 | 569.2023 | 1423.0057 | 142.3006 | 0 | 13.0905 | 2950 | 2950 | 30 | 10 | D | 5 | 10 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 5809.2785 |  | 85810.1664 | 241341.093 | 30527.0889 | 274743.8001 | 54987.0736 | 632422.1484 | 687409.2221 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -6639.1754 |  | -10514.9419 | -29573.2742 | -3740.7056 | 5578.9929 | -18051.4434 | -38249.9289 | -56301.3723
[21 empty] | 1144.1108 | 9006.4402 | 22516.1005 | 2251.6101 | 0 | 207.1304 | 46925 | 46925 | 484 | 159 |  | 78.5 | 159
Zoning Area AHU - 4 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
51 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
52 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 96.84 | 762.3245 | 1016.4326 | 101.6433 | 0 | 9.3504 | 2350 | 2350 | 10 | 6 | C | 4 | 6 | 36500 | W | 150 | 1120 | 50 | 4 | 94 | 3 | 376 | 23.7218 | 2 | 122.9205 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 4149.4846 |  | 42905.0832 | 241341.093 | 21805.0635 | 196245.5715 | 45953.7511 | 502296.8112 | 548250.5624 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -4742.2681 |  | -5257.471 | -29573.2742 | -2671.9325 | 3984.9949 | -420.2656 | -33517.6828 | -33937.9484
53 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 42.6096 | 335.4228 | 447.2304 | 44.723 | 0 | 4.1142 | 1975 | 1975 | 8 | 5 | C | 4.5 | 5 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 1825.7732 |  | 85810.1664 | 241341.093 | 9594.2279 | 86348.0514 | 49772.0051 | 423093.5389 | 472865.5439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -2086.598 |  | -10514.9419 | -29573.2742 | -1175.6503 | 1753.3978 | -12086.4649 | -39510.4687 | -51596.9337
54 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 45.192 | 355.7514 | 474.3352 | 47.4335 | 0 | 4.3635 | 2000 | 2000 | 8 | 5 | C | 5 | 5 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 1936.4262 |  | 85810.1664 | 241341.093 | 10175.6963 | 91581.2667 | 56985.6372 | 428908.2225 | 485893.8597 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -2213.0585 |  | -10514.9419 | -29573.2742 | -1246.9019 | 1859.6643 | -5708.185 | -39475.4537 | -45183.6387
55 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 79.086 | 622.565 | 830.0867 | 83.0087 | 0 | 7.6361 | 1975 | 1975 | 8 | 5 | C | 2.5 | 5 |  | 2900 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 3388.7458 |  | 0 | 241341.093 | 17807.4685 | 160267.2167 | 29688.7502 | 419415.7783 | 449104.5284 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -3872.8523 |  | 0 | -29573.2742 | -2182.0782 | 3254.4125 | 10859.8078 | -28500.94 | -17641.1322
56 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 116.208 | 914.7894 | 1219.7192 | 121.9719 | 0 | 11.2205 | 2750 | 2750 | 12 | 7 | C | 5 | 7 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 4979.3815 |  | 85810.1664 | 241341.093 | 26166.0762 | 235494.6858 | 55737.1071 | 588812.0214 | 644549.1285 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -5690.7218 |  | -10514.9419 | -29573.2742 | -3206.3191 | 4781.9939 | -18915.8682 | -38512.5413 | -57428.4095
57 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 171.7296 | 1351.8554 | 1802.4739 | 180.2474 | 0 | 16.5813 | 3550 | 3550 | 16 | 9 | C | 7 | 9 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 7358.4194 |  | 128715.2496 | 241341.093 | 38667.6459 | 348008.8134 | 78048.5967 | 756732.802 | 834781.3987 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -8409.6221 |  | -15772.4129 | -29573.2742 | -4738.2271 | 7066.7243 | -29801.0173 | -43017.1899 | -72818.2072
58 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 86.7256 | 682.7039 | 910.2719 | 91.0272 | 0 | 8.3738 | 2450 | 2450 | 10 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 3716.094 |  | 85810.1664 | 241341.093 | 19527.6458 | 175748.8118 | 53419.2477 | 522427.717 | 575846.9647 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -4246.9646 |  | -10514.9419 | -29573.2742 | -2392.864 | 3568.7843 | -16262.0214 | -38912.2959 | -55174.3172
59 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 49.0656 | 386.2444 | 514.9925 | 51.4993 | 0 | 4.7375 | 2250 | 2250 | 10 | 6 | C | 5.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 2102.4055 |  | 128715.2496 | 241341.093 | 11047.8988 | 99431.0895 | 65397.5859 | 480535.3311 | 545932.917 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -2402.7492 |  | -15772.4129 | -29573.2742 | -1353.7792 | 2019.0641 | -22633.9083 | -44680.4022 | -67314.3105
60 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 93.612 | 736.9137 | 982.5516 | 98.2552 | 0 | 9.0387 | 2525 | 2525 | 12 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 4011.1685 |  | 85810.1664 | 241341.093 | 21078.228 | 189704.0524 | 53931.1473 | 537933.5399 | 591864.6873 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -4584.1925 |  | -10514.9419 | -29573.2742 | -2582.8681 | 3852.1617 | -16848.1858 | -38818.9225 | -55667.1083
61 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 51.648 | 406.5731 | 542.0974 | 54.2097 | 0 | 4.9869 | 2075 | 2075 | 10 | 5.5 | C | 4.5 | 5.5 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 2213.0585 |  | 85810.1664 | 241341.093 | 11629.3672 | 104664.3048 | 50564.6716 | 443444.9314 | 494009.603 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -2529.2097 |  | -10514.9419 | -29573.2742 | -1425.0307 | 2125.3306 | -12993.8609 | -39387.9162 | -52381.7771
62 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 40.6728 | 320.1763 | 426.9017 | 42.6902 | 0 | 3.9272 | 1975 | 1975 | 8 | 5 | C | 4.5 | 5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 1742.7835 |  | 85810.1664 | 241341.093 | 9158.1267 | 82423.14 | 49589.5975 | 418732.5262 | 468322.1236 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -1991.7526 |  | -10514.9419 | -29573.2742 | -1122.2117 | 1673.6979 | -11877.6796 | -39536.73 | -51414.4095
63 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 36.7992 | 289.6833 | 386.2444 | 38.6244 | 0 | 3.5531 | 1925 | 1925 | 8 | 5 | C | 4.5 | 5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 1576.8042 |  | 85810.1664 | 241341.093 | 8285.9241 | 74573.3172 | 49224.7824 | 410010.5008 | 459235.2831 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -1802.0619 |  | -10514.9419 | -29573.2742 | -1015.3344 | 1514.2981 | -11460.1088 | -39589.2525 | -51049.3613
64 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 40.888 | 321.8703 | 429.1604 | 42.916 | 0 | 3.9479 | 1975 | 1975 | 8 | 5 | C | 4.5 | 5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 1752.0046 |  | 85810.1664 | 241341.093 | 9206.5824 | 82859.2413 | 49600.1035 | 419217.0831 | 468817.1867 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -2002.291 |  | -10514.9419 | -29573.2742 | -1128.1493 | 1682.5534 | -11889.722 | -39533.812 | -51423.534
65 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 54.4456 | 428.5958 | 571.461 | 57.1461 | 0 | 5.257 | 2100 | 2100 | 10 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 2332.9325 |  | 85810.1664 | 241341.093 | 12259.2913 | 110333.6213 | 50789.1033 | 449744.172 | 500533.2753 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -2666.2085 |  | -10514.9419 | -29573.2742 | -1502.2199 | 2240.4527 | -13250.8159 | -39349.9833 | -52600.7992
66 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 66.2816 | 521.7688 | 695.6917 | 69.5692 | 0 | 6.3998 | 2225 | 2225 | 10 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 2840.0917 |  | 85810.1664 | 241341.093 | 14924.3546 | 134319.1911 | 51806.2015 | 476394.8052 | 528201.0067 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -3245.8191 |  | -10514.9419 | -29573.2742 | -1828.7894 | 2727.5076 | -14415.1668 | -39189.4979 | -53604.6647
67 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 10K | 80 | 0 | 100 | 10K | 80 | 72.3072 | 569.2023 | 758.9364 | 75.8936 | 0 | 6.9816 | 2300 | 2300 | 10 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 3098.2818 |  | 85810.1664 | 241341.093 | 16281.1141 | 146530.0267 | 52276.077 | 489962.4002 | 542238.4773 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -3540.8935 |  | -10514.9419 | -29573.2742 | -1995.043 | 2975.4629 | -14953.1616 | -39107.7963 | -54060.9578
[21 empty] | 1144.1108 | 9006.4402 | 12008.587 | 1200.8587 | 0 | 110.4695 | 36400 | 36400 | 158 | 94 |  | 74 | 94
Zoning Area AHU - 5 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
68 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
69 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 96.84 | 762.3245 | 254.1082 | 25.4108 | 0 | 2.3376 | 1600 | 1600 | 6 | 4 | C | 4 | 4 | 27500 | W | 150 | 1000 | 40 | 4 | 74.5 | 3 | 292 | 18.4223 | 2 | 108.3233 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 1037.3712 |  | 42905.0832 | 241341.093 | 5451.2659 | 49061.3929 | 42841.6377 | 338758.835 | 381600.4727 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -1185.567 |  | -5257.471 | -29573.2742 | -667.9831 | 996.2487 | 3136.4355 | -34502.4796 | -31366.0441
70 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 42.6096 | 335.4228 | 111.8076 | 11.1808 | 0 | 1.0285 | 1650 | 1650 | 6 | 4.5 | C | 4.5 | 4.5 |  | 2900 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 456.4433 |  | 85810.1664 | 241341.093 | 2398.557 | 21587.0129 | 48402.6751 | 351136.8293 | 399539.5045 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -521.6495 |  | -10514.9419 | -29573.2742 | -293.9126 | 438.3494 | -10521.5165 | -39943.7793 | -50465.2958
71 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 45.192 | 355.7514 | 118.5838 | 11.8584 | 0 | 1.0909 | 1650 | 1650 | 6 | 5 | C | 5 | 4.5 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 484.1065 |  | 85810.1664 | 241341.093 | 2543.9241 | 22895.3167 | 55533.3176 | 352590.5002 | 408123.8178 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -553.2646 |  | -10514.9419 | -29573.2742 | -311.7255 | 464.9161 | -4048.3911 | -39935.0255 | -43983.4167
72 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 79.086 | 622.565 | 207.5217 | 20.7522 | 0 | 1.909 | 1350 | 1350 | 4 | 3.5 | C | 2.5 | 3.5 |  | 2900 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 847.1864 |  | 0 | 241341.093 | 4451.8671 | 40066.8042 | 27147.1908 | 285859.7644 | 313006.9552 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -968.2131 |  | 0 | -29573.2742 | -545.5196 | 813.6031 | 13764.447 | -29305.1906 | -15540.7436
73 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 116.208 | 914.7894 | 304.9298 | 30.493 | 0 | 2.8051 | 1850 | 1850 | 6 | 5 | C | 4.5 | 5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 1244.8454 |  | 85810.1664 | 241341.093 | 6541.519 | 58873.6714 | 52002.571 | 392566.45 | 444569.0209 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -1422.6804 |  | -10514.9419 | -29573.2742 | -801.5798 | 1195.4985 | -14647.8269 | -39694.2974 | -54342.1243
74 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 171.7296 | 1351.8554 | 450.6185 | 45.0618 | 0 | 4.1453 | 2200 | 2200 | 8 | 6.5 | C | 6.5 | 5.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 1839.6048 |  | 128715.2496 | 241341.093 | 9666.9115 | 87002.2034 | 72529.7821 | 466725.4575 | 539255.2396 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -2102.4055 |  | -15772.4129 | -29573.2742 | -1184.5568 | 1766.6811 | -23493.8007 | -44763.5628 | -68257.3635
75 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 86.7256 | 682.7039 | 227.568 | 22.7568 | 0 | 2.0934 | 1775 | 1775 | 6 | 4.5 | C | 4.5 | 4.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 929.0235 |  | 85810.1664 | 241341.093 | 4881.9114 | 43937.2029 | 50632.1772 | 375970.3738 | 426602.551 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -1061.7411 |  | -10514.9419 | -29573.2742 | -598.216 | 892.1961 | -13076.7979 | -39794.2361 | -52871.034
76 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 49.0656 | 386.2444 | 128.7481 | 12.8748 | 0 | 1.1844 | 1875 | 1875 | 6 | 5.5 | C | 5.5 | 5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 525.6014 |  | 128715.2496 | 241341.093 | 2761.9747 | 24857.7724 | 63820.7817 | 397676.0898 | 461496.8715 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -600.6873 |  | -15772.4129 | -29573.2742 | -338.4448 | 504.766 | -20831.8464 | -45179.3659 | -66011.2123
77 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 93.612 | 736.9137 | 245.6379 | 24.5638 | 0 | 2.2597 | 1775 | 1775 | 6 | 4.5 | C | 4.5 | 4.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 1002.7921 |  | 85810.1664 | 241341.093 | 5269.557 | 47426.0131 | 50922.771 | 379846.8296 | 430769.6006 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -1146.0481 |  | -10514.9419 | -29573.2742 | -645.717 | 963.0404 | -13410.0414 | -39770.8927 | -53180.9341
78 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 51.648 | 406.5731 | 135.5244 | 13.5524 | 0 | 1.2467 | 1675 | 1675 | 6 | 4.5 | C | 4.5 | 4.5 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 553.2646 |  | 85810.1664 | 241341.093 | 2907.3418 | 26166.0762 | 48904.8777 | 356224.6775 | 405129.5552 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -632.3024 |  | -10514.9419 | -29573.2742 | -356.2577 | 531.3327 | -11096.9536 | -39913.1412 | -51010.0948
79 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 40.6728 | 320.1763 | 106.7254 | 10.6725 | 0 | 0.98179 | 1650 | 1650 | 6 | 4.5 | C | 4.5 | 4.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 435.6959 |  | 85810.1664 | 241341.093 | 2289.5317 | 20605.785 | 48282.5098 | 350046.5761 | 398329.086 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -497.9382 |  | -10514.9419 | -29573.2742 | -280.5529 | 418.4245 | -10383.8651 | -39950.3446 | -50334.2097
80 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 36.7992 | 289.6833 | 96.5611 | 9.6561 | 0 | 0.88829 | 1625 | 1625 | 6 | 4.5 | C | 4.5 | 4.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 394.201 |  | 85810.1664 | 241341.093 | 2071.481 | 18643.3293 | 48042.1792 | 347866.0698 | 395908.249 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -450.5155 |  | -10514.9419 | -29573.2742 | -253.8336 | 378.5745 | -10108.5624 | -39963.4752 | -50072.0376
81 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 40.888 | 321.8703 | 107.2901 | 10.729 | 0 | 0.98698 | 1650 | 1650 | 6 | 4.5 | C | 4.5 | 4.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 438.0012 |  | 85810.1664 | 241341.093 | 2301.6456 | 20714.8103 | 48286.1001 | 350167.7154 | 398453.8155 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -500.5727 |  | -10514.9419 | -29573.2742 | -282.0373 | 420.6384 | -10388.0037 | -39949.6151 | -50337.6189
82 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 54.4456 | 428.5958 | 142.8653 | 14.2865 | 0 | 1.3142 | 1675 | 1675 | 6 | 4.5 | C | 4.5 | 4.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 583.2331 |  | 85810.1664 | 241341.093 | 3064.8228 | 27583.4053 | 49039.404 | 357799.4876 | 406838.8916 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -666.5521 |  | -10514.9419 | -29573.2742 | -375.555 | 560.1132 | -11251.1595 | -39903.6579 | -51154.8174
83 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 66.2816 | 521.7688 | 173.9229 | 17.3923 | 0 | 1.6 | 1700 | 1700 | 6 | 4.5 | C | 4.5 | 4.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 710.0229 |  | 85810.1664 | 241341.093 | 3731.0886 | 33579.7978 | 49676.1328 | 364462.1459 | 414138.2786 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -811.4548 |  | -10514.9419 | -29573.2742 | -457.1973 | 681.8769 | -11980.8025 | -39863.5366 | -51844.3391
84 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | NC | 20 | 0 | 100 | NC | 20 | 72.3072 | 569.2023 | 189.7341 | 18.9734 | 0 | 1.7454 | 1725 | 1725 | 6 | 4.5 | C | 4.5 | 4.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 774.5705 |  | 85810.1664 | 241341.093 | 4070.2785 | 36632.5067 | 49952.3656 | 367854.0447 | 417806.4103 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -885.2234 |  | -10514.9419 | -29573.2742 | -498.7607 | 743.8657 | -12297.4914 | -39843.1112 | -52140.6026
[21 empty] | 1144.1108 | 9006.4402 | 3002.1467 | 300.2147 | 0 | 27.6174 | 27425 | 27425 | 96 | 74.5 |  | 73 | 72.5
Zoning Area AHU - 6 Air-Conditioning System (DX) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
85 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
86 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 96.84 | 762.3245 | 317.6352 | 31.7635 | 0 | 2.922 | 1650 | 1650 | 6 | 5.5 | D | 4 | 5.5 | 28250 | W | 150 | 1000 | 40 | 6 | 98 | 3 | 392 | 24.7313 | 2 | 125.5086 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 1296.7139 |  | 42905.0832 | 241341.093 | 6814.0823 | 61326.7411 | 43100.9805 | 352386.9997 | 395487.9801 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -1481.9588 |  | -5257.471 | -29573.2742 | -834.9789 | 1245.3109 | 2840.0437 | -34420.4132 | -31580.3695
87 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 42.6096 | 335.4228 | 139.7595 | 13.9759 | 0 | 1.2857 | 1675 | 1675 | 6 | 6 | D | 4.5 | 6 |  | 2900 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 570.5541 |  | 85810.1664 | 241341.093 | 2998.1962 | 26983.7661 | 48516.786 | 357133.2218 | 405650.0077 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -652.0619 |  | -10514.9419 | -29573.2742 | -367.3907 | 547.9368 | -10651.9288 | -39907.6701 | -50559.5989
88 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 45.192 | 355.7514 | 148.2298 | 14.823 | 0 | 1.3636 | 1675 | 1675 | 6 | 6 | D | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 605.1332 |  | 85810.1664 | 241341.093 | 3179.9051 | 28619.1458 | 55654.3443 | 358950.3104 | 414604.6547 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -691.5808 |  | -10514.9419 | -29573.2742 | -389.6568 | 581.1451 | -4186.7073 | -39896.7279 | -44083.4352
89 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 79.086 | 622.565 | 259.4021 | 25.9402 | 0 | 2.3863 | 1400 | 1400 | 4 | 5 | D | 2.5 | 5 |  | 2900 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 1058.9831 |  | 0 | 241341.093 | 5564.8339 | 50083.5052 | 27358.9874 | 296989.4322 | 324348.4196 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -1210.2663 |  | 0 | -29573.2742 | -681.8995 | 1017.0039 | 13522.3937 | -29238.1698 | -15715.776
90 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 116.208 | 914.7894 | 381.1622 | 38.1162 | 0 | 3.5064 | 1925 | 1925 | 6 | 6.5 | D | 4.5 | 6.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 1556.0567 |  | 85810.1664 | 241341.093 | 8176.8988 | 73592.0893 | 52313.7823 | 408920.2476 | 461234.0299 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -1778.3505 |  | -10514.9419 | -29573.2742 | -1001.9747 | 1494.3731 | -15003.497 | -39595.8178 | -54599.3147
91 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 171.7296 | 1351.8554 | 563.2731 | 56.3273 | 0 | 5.1817 | 2300 | 2300 | 8 | 8 | D | 6.5 | 8 |  | 6000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 2299.5061 |  | 128715.2496 | 241341.093 | 12083.6394 | 108752.7542 | 72989.6833 | 490892.7362 | 563882.4196 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -2628.0069 |  | -15772.4129 | -29573.2742 | -1480.696 | 2208.3513 | -24019.4021 | -44618.0317 | -68637.4338
92 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 86.7256 | 682.7039 | 284.46 | 28.446 | 0 | 2.6168 | 1825 | 1825 | 6 | 6.5 | D | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 1161.2794 |  | 85810.1664 | 241341.093 | 6102.3893 | 54921.5037 | 50864.4331 | 388175.1524 | 439039.5855 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -1327.1764 |  | -10514.9419 | -29573.2742 | -747.77 | 1115.2451 | -13342.2332 | -39720.7411 | -53062.9743
93 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 49.0656 | 386.2444 | 160.9352 | 16.0935 | 0 | 1.4805 | 1900 | 1900 | 6 | 6.5 | D | 5.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 657.0017 |  | 128715.2496 | 241341.093 | 3452.4684 | 31072.2155 | 63952.1821 | 404581.0265 | 468533.2086 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -750.8591 |  | -15772.4129 | -29573.2742 | -423.056 | 630.9575 | -20982.0182 | -45137.7856 | -66119.8038
94 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 93.612 | 736.9137 | 307.0474 | 30.7047 | 0 | 2.8246 | 1850 | 1850 | 6 | 6.5 | D | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 1253.4901 |  | 85810.1664 | 241341.093 | 6586.9463 | 59282.5164 | 51173.469 | 393020.7221 | 444194.1911 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -1432.5602 |  | -10514.9419 | -29573.2742 | -807.1463 | 1203.8005 | -13696.5534 | -39691.5619 | -53388.1153
95 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 51.648 | 406.5731 | 169.4054 | 16.9405 | 0 | 1.5584 | 1700 | 1700 | 6 | 6 | D | 4.5 | 6 |  | 5600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 691.5808 |  | 85810.1664 | 241341.093 | 3634.1772 | 32707.5952 | 49043.1939 | 363493.032 | 412536.2258 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -790.378 |  | -10514.9419 | -29573.2742 | -445.3221 | 664.1658 | -11255.0292 | -39869.3724 | -51124.4016
96 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 40.6728 | 320.1763 | 133.4068 | 13.3407 | 0 | 1.2272 | 1675 | 1675 | 6 | 6 | D | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 544.6199 |  | 85810.1664 | 241341.093 | 2861.9146 | 25757.2313 | 48391.4338 | 355770.4053 | 404161.8391 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -622.4227 |  | -10514.9419 | -29573.2742 | -350.6911 | 523.0306 | -10508.3497 | -39915.8767 | -50424.2264
97 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 36.7992 | 289.6833 | 120.7014 | 12.0701 | 0 | 1.1104 | 1650 | 1650 | 6 | 5.5 | D | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 492.7513 |  | 85810.1664 | 241341.093 | 2589.3513 | 23304.1616 | 48140.7295 | 353044.7724 | 401185.5019 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -563.1443 |  | -10514.9419 | -29573.2742 | -317.292 | 473.2181 | -10221.1913 | -39932.29 | -50153.4813
98 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 40.888 | 321.8703 | 134.1126 | 13.4113 | 0 | 1.2337 | 1675 | 1675 | 6 | 6 | D | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 547.5014 |  | 85810.1664 | 241341.093 | 2877.057 | 25893.5129 | 48395.6004 | 355921.8294 | 404317.4297 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -625.7159 |  | -10514.9419 | -29573.2742 | -352.5467 | 525.7979 | -10513.1469 | -39914.9649 | -50428.1118
99 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 54.4456 | 428.5958 | 178.5816 | 17.8582 | 0 | 1.6428 | 1725 | 1725 | 6 | 6 | D | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 729.0414 |  | 85810.1664 | 241341.093 | 3831.0285 | 34479.2567 | 49185.2122 | 365461.5446 | 414646.7569 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -833.1902 |  | -10514.9419 | -29573.2742 | -469.4437 | 700.1415 | -11417.7975 | -39857.5184 | -51275.3159
100 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 66.2816 | 521.7688 | 217.4036 | 21.7404 | 0 | 1.9999 | 1750 | 1750 | 6 | 6 | D | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 887.5287 |  | 85810.1664 | 241341.093 | 4663.8608 | 41974.7472 | 49853.6385 | 373789.8675 | 423643.506 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -1014.3185 |  | -10514.9419 | -29573.2742 | -571.4967 | 852.3461 | -12183.6662 | -39807.3667 | -51991.0329
101 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | 5 Micron | 25 | 0 | 100 | 5 Micron | 25 | 72.3072 | 569.2023 | 237.1676 | 23.7168 | 0 | 2.1818 | 1775 | 1775 | 6 | 6 | D | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 968.2131 |  | 85810.1664 | 241341.093 | 5087.8481 | 45790.6333 | 50146.0083 | 378029.741 | 428175.7492 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -1106.5292 |  | -10514.9419 | -29573.2742 | -623.4509 | 929.8321 | -12518.7973 | -39781.8349 | -52300.6322
[21 empty] | 1144.1108 | 9006.4402 | 3752.6834 | 375.2683 | 0 | 34.5217 | 28150 | 28150 | 96 | 98 |  | 73 | 98
Zoning Area AHU - 7 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
102 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
103 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.0256 | 2850 | 2850 | 18 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 3 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 6224.2269 |  | 42905.0832 | 241341.093 | 32707.5952 | 294368.3572 | 48028.4934 | 611322.1287 | 659350.6222 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -7113.4022 |  | -5257.471 | -29573.2742 | -4007.8988 | 5977.4923 | -2791.3997 | -32861.1517 | -35652.5513
104 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.1712 | 2200 | 2200 | 14 | 5.5 | C | 4.5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 2738.6598 |  | 85810.1664 | 241341.093 | 14391.3419 | 129522.0772 | 50684.8917 | 471064.6785 | 521749.5702 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3129.897 |  | -10514.9419 | -29573.2742 | -1763.4755 | 2630.0966 | -13129.7639 | -39221.595 | -52351.3589
105 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.5453 | 2250 | 2250 | 14 | 6 | C | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 2904.6392 |  | 85810.1664 | 241341.093 | 15263.5444 | 137371.9 | 57953.8503 | 479786.7039 | 537740.5543 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -3319.5877 |  | -10514.9419 | -29573.2742 | -1870.3528 | 2789.4964 | -6814.7142 | -39169.0725 | -45983.7867
106 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.4542 | 2375 | 2375 | 14 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 5083.1186 |  | 0 | 241341.093 | 26711.2028 | 240400.8251 | 31383.123 | 508453.1209 | 539836.2439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -5809.2785 |  | 0 | -29573.2742 | -3273.1174 | 4881.6187 | 8923.3816 | -27964.7728 | -19041.3912
107 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 16.8307 | 3375 | 3375 | 20 | 8.5 | C | 5 | 8.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 7469.0723 |  | 85810.1664 | 241341.093 | 39249.1143 | 353242.0287 | 58226.7979 | 719642.4024 | 777869.2003 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -8536.0826 |  | -10514.9419 | -29573.2742 | -4809.4786 | 7172.9908 | -21761.229 | -37724.7039 | -59485.933
108 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 24.872 | 4450 | 4450 | 26 | 11.5 | C | 7 | 11.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 11037.6291 |  | 128715.2496 | 241341.093 | 58001.4689 | 522013.2201 | 81727.8063 | 950071.0317 | 1031798.838 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -12614.4332 |  | -15772.4129 | -29573.2742 | -7107.3406 | 10600.0864 | -34005.8283 | -41852.9413 | -75858.7696
109 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.5607 | 2900 | 2900 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 5574.141 |  | 85810.1664 | 241341.093 | 29291.4686 | 263623.2177 | 55277.2947 | 620065.9458 | 675343.2405 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -6370.4468 |  | -10514.9419 | -29573.2742 | -3589.2961 | 5353.1765 | -18385.5037 | -38324.3357 | -56709.8394
110 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.1063 | 2500 | 2500 | 16 | 6.5 | C | 6 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3153.6083 |  | 128715.2496 | 241341.093 | 16571.8483 | 149146.6343 | 66448.7887 | 535774.8253 | 602223.6139 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -3604.1238 |  | -15772.4129 | -29573.2742 | -2030.6687 | 3028.5961 | -23835.2829 | -44347.7597 | -68183.0426
111 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 13.558 | 3000 | 3000 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 6016.7527 |  | 85810.1664 | 241341.093 | 31617.3421 | 284556.0786 | 55936.7316 | 643324.6802 | 699261.4117 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -6876.2888 |  | -10514.9419 | -29573.2742 | -3874.3022 | 5778.2426 | -19140.2821 | -38184.2757 | -57324.5578
112 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.4803 | 2350 | 2350 | 14 | 6 | C | 4.5 | 6 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 3319.5877 |  | 85810.1664 | 241341.093 | 17444.0508 | 156996.4572 | 51671.2008 | 501591.7674 | 553262.9683 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -3793.8145 |  | -10514.9419 | -29573.2742 | -2137.546 | 3187.9959 | -14258.4657 | -39037.7663 | -53296.232
113 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 5.8907 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 2614.1753 |  | 85810.1664 | 241341.093 | 13737.19 | 123634.71 | 50460.9893 | 464523.1595 | 514984.1488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -2987.6289 |  | -10514.9419 | -29573.2742 | -1683.3175 | 2510.5468 | -12873.5559 | -39260.9869 | -52134.5428
114 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.3297 | 2125 | 2125 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2365.2062 |  | 85810.1664 | 241341.093 | 12428.8862 | 111859.9757 | 50013.1844 | 451440.1214 | 501453.3058 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -2703.0928 |  | -10514.9419 | -29573.2742 | -1523.0016 | 2271.4471 | -12361.1398 | -39339.7706 | -51700.9104
115 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 5.9219 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 2628.0069 |  | 85810.1664 | 241341.093 | 13809.8735 | 124288.8619 | 50476.1058 | 465249.9949 | 515726.1008 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3003.4365 |  | -10514.9419 | -29573.2742 | -1692.2239 | 2523.8301 | -12890.8675 | -39256.61 | -52147.4775
116 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 7.8855 | 2400 | 2400 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 3499.3987 |  | 85810.1664 | 241341.093 | 18388.9369 | 165500.4319 | 51955.5695 | 511040.6283 | 562996.1978 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -3999.3128 |  | -10514.9419 | -29573.2742 | -2253.3298 | 3360.679 | -14583.9201 | -38980.8669 | -53564.787
117 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.5997 | 2575 | 2575 | 16 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 4260.1375 |  | 85810.1664 | 241341.093 | 22386.5319 | 201478.7867 | 53226.2474 | 551016.578 | 604242.8254 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -4868.7286 |  | -10514.9419 | -29573.2742 | -2743.1841 | 4091.2614 | -16038.0763 | -38740.1388 | -54778.2151
118 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.4724 | 2675 | 2675 | 16 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 4647.4228 |  | 85810.1664 | 241341.093 | 24421.6711 | 219795.0401 | 53825.2179 | 571367.9706 | 625193.1886 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -5311.3403 |  | -10514.9419 | -29573.2742 | -2992.5645 | 4463.1943 | -16723.6083 | -38617.5863 | -55341.1947
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 165.7043 | 42375 | 42375 | 260 | 108.5 |  | 76.5 | 108.5
Zoning Area AHU - 8 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
119 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
120 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.0256 | 2850 | 2850 | 18 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 3 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 6224.2269 |  | 42905.0832 | 241341.093 | 32707.5952 | 294368.3572 | 48028.4934 | 611322.1287 | 659350.6222 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -7113.4022 |  | -5257.471 | -29573.2742 | -4007.8988 | 5977.4923 | -2791.3997 | -32861.1517 | -35652.5513
121 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.1712 | 2200 | 2200 | 14 | 5.5 | C | 4.5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 2738.6598 |  | 85810.1664 | 241341.093 | 14391.3419 | 129522.0772 | 50684.8917 | 471064.6785 | 521749.5702 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3129.897 |  | -10514.9419 | -29573.2742 | -1763.4755 | 2630.0966 | -13129.7639 | -39221.595 | -52351.3589
122 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.5453 | 2250 | 2250 | 14 | 6 | C | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 2904.6392 |  | 85810.1664 | 241341.093 | 15263.5444 | 137371.9 | 57953.8503 | 479786.7039 | 537740.5543 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -3319.5877 |  | -10514.9419 | -29573.2742 | -1870.3528 | 2789.4964 | -6814.7142 | -39169.0725 | -45983.7867
123 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.4542 | 2375 | 2375 | 14 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 5083.1186 |  | 0 | 241341.093 | 26711.2028 | 240400.8251 | 31383.123 | 508453.1209 | 539836.2439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -5809.2785 |  | 0 | -29573.2742 | -3273.1174 | 4881.6187 | 8923.3816 | -27964.7728 | -19041.3912
124 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 16.8307 | 3375 | 3375 | 20 | 8.5 | C | 5 | 8.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 7469.0723 |  | 85810.1664 | 241341.093 | 39249.1143 | 353242.0287 | 58226.7979 | 719642.4024 | 777869.2003 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -8536.0826 |  | -10514.9419 | -29573.2742 | -4809.4786 | 7172.9908 | -21761.229 | -37724.7039 | -59485.933
125 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 24.872 | 4450 | 4450 | 26 | 11.5 | C | 7 | 11.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 11037.6291 |  | 128715.2496 | 241341.093 | 58001.4689 | 522013.2201 | 81727.8063 | 950071.0317 | 1031798.838 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -12614.4332 |  | -15772.4129 | -29573.2742 | -7107.3406 | 10600.0864 | -34005.8283 | -41852.9413 | -75858.7696
126 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.5607 | 2900 | 2900 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 5574.141 |  | 85810.1664 | 241341.093 | 29291.4686 | 263623.2177 | 55277.2947 | 620065.9458 | 675343.2405 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -6370.4468 |  | -10514.9419 | -29573.2742 | -3589.2961 | 5353.1765 | -18385.5037 | -38324.3357 | -56709.8394
127 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.1063 | 2500 | 2500 | 16 | 6.5 | C | 6 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3153.6083 |  | 128715.2496 | 241341.093 | 16571.8483 | 149146.6343 | 66448.7887 | 535774.8253 | 602223.6139 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -3604.1238 |  | -15772.4129 | -29573.2742 | -2030.6687 | 3028.5961 | -23835.2829 | -44347.7597 | -68183.0426
128 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 13.558 | 3000 | 3000 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 6016.7527 |  | 85810.1664 | 241341.093 | 31617.3421 | 284556.0786 | 55936.7316 | 643324.6802 | 699261.4117 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -6876.2888 |  | -10514.9419 | -29573.2742 | -3874.3022 | 5778.2426 | -19140.2821 | -38184.2757 | -57324.5578
129 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.4803 | 2350 | 2350 | 14 | 6 | C | 4.5 | 6 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 3319.5877 |  | 85810.1664 | 241341.093 | 17444.0508 | 156996.4572 | 51671.2008 | 501591.7674 | 553262.9683 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -3793.8145 |  | -10514.9419 | -29573.2742 | -2137.546 | 3187.9959 | -14258.4657 | -39037.7663 | -53296.232
130 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 5.8907 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 2614.1753 |  | 85810.1664 | 241341.093 | 13737.19 | 123634.71 | 50460.9893 | 464523.1595 | 514984.1488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -2987.6289 |  | -10514.9419 | -29573.2742 | -1683.3175 | 2510.5468 | -12873.5559 | -39260.9869 | -52134.5428
131 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.3297 | 2125 | 2125 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2365.2062 |  | 85810.1664 | 241341.093 | 12428.8862 | 111859.9757 | 50013.1844 | 451440.1214 | 501453.3058 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -2703.0928 |  | -10514.9419 | -29573.2742 | -1523.0016 | 2271.4471 | -12361.1398 | -39339.7706 | -51700.9104
132 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 5.9219 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 2628.0069 |  | 85810.1664 | 241341.093 | 13809.8735 | 124288.8619 | 50476.1058 | 465249.9949 | 515726.1008 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3003.4365 |  | -10514.9419 | -29573.2742 | -1692.2239 | 2523.8301 | -12890.8675 | -39256.61 | -52147.4775
133 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 7.8855 | 2400 | 2400 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 3499.3987 |  | 85810.1664 | 241341.093 | 18388.9369 | 165500.4319 | 51955.5695 | 511040.6283 | 562996.1978 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -3999.3128 |  | -10514.9419 | -29573.2742 | -2253.3298 | 3360.679 | -14583.9201 | -38980.8669 | -53564.787
134 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.5997 | 2575 | 2575 | 16 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 4260.1375 |  | 85810.1664 | 241341.093 | 22386.5319 | 201478.7867 | 53226.2474 | 551016.578 | 604242.8254 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -4868.7286 |  | -10514.9419 | -29573.2742 | -2743.1841 | 4091.2614 | -16038.0763 | -38740.1388 | -54778.2151
135 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.4724 | 2675 | 2675 | 16 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 4647.4228 |  | 85810.1664 | 241341.093 | 24421.6711 | 219795.0401 | 53825.2179 | 571367.9706 | 625193.1886 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -5311.3403 |  | -10514.9419 | -29573.2742 | -2992.5645 | 4463.1943 | -16723.6083 | -38617.5863 | -55341.1947
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 165.7043 | 42375 | 42375 | 260 | 108.5 |  | 76.5 | 108.5
Zoning Area AHU - 9 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
136 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
137 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.0256 | 2850 | 2850 | 18 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 3 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 6224.2269 |  | 42905.0832 | 241341.093 | 32707.5952 | 294368.3572 | 48028.4934 | 611322.1287 | 659350.6222 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -7113.4022 |  | -5257.471 | -29573.2742 | -4007.8988 | 5977.4923 | -2791.3997 | -32861.1517 | -35652.5513
138 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.1712 | 2200 | 2200 | 14 | 5.5 | C | 4.5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 2738.6598 |  | 85810.1664 | 241341.093 | 14391.3419 | 129522.0772 | 50684.8917 | 471064.6785 | 521749.5702 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3129.897 |  | -10514.9419 | -29573.2742 | -1763.4755 | 2630.0966 | -13129.7639 | -39221.595 | -52351.3589
139 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.5453 | 2250 | 2250 | 14 | 6 | C | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 2904.6392 |  | 85810.1664 | 241341.093 | 15263.5444 | 137371.9 | 57953.8503 | 479786.7039 | 537740.5543 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -3319.5877 |  | -10514.9419 | -29573.2742 | -1870.3528 | 2789.4964 | -6814.7142 | -39169.0725 | -45983.7867
140 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.4542 | 2375 | 2375 | 14 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 5083.1186 |  | 0 | 241341.093 | 26711.2028 | 240400.8251 | 31383.123 | 508453.1209 | 539836.2439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -5809.2785 |  | 0 | -29573.2742 | -3273.1174 | 4881.6187 | 8923.3816 | -27964.7728 | -19041.3912
141 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 16.8307 | 3375 | 3375 | 20 | 8.5 | C | 5 | 8.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 7469.0723 |  | 85810.1664 | 241341.093 | 39249.1143 | 353242.0287 | 58226.7979 | 719642.4024 | 777869.2003 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -8536.0826 |  | -10514.9419 | -29573.2742 | -4809.4786 | 7172.9908 | -21761.229 | -37724.7039 | -59485.933
142 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 24.872 | 4450 | 4450 | 26 | 11.5 | C | 7 | 11.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 11037.6291 |  | 128715.2496 | 241341.093 | 58001.4689 | 522013.2201 | 81727.8063 | 950071.0317 | 1031798.838 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -12614.4332 |  | -15772.4129 | -29573.2742 | -7107.3406 | 10600.0864 | -34005.8283 | -41852.9413 | -75858.7696
143 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.5607 | 2900 | 2900 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 5574.141 |  | 85810.1664 | 241341.093 | 29291.4686 | 263623.2177 | 55277.2947 | 620065.9458 | 675343.2405 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -6370.4468 |  | -10514.9419 | -29573.2742 | -3589.2961 | 5353.1765 | -18385.5037 | -38324.3357 | -56709.8394
144 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.1063 | 2500 | 2500 | 16 | 6.5 | C | 6 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3153.6083 |  | 128715.2496 | 241341.093 | 16571.8483 | 149146.6343 | 66448.7887 | 535774.8253 | 602223.6139 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -3604.1238 |  | -15772.4129 | -29573.2742 | -2030.6687 | 3028.5961 | -23835.2829 | -44347.7597 | -68183.0426
145 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 13.558 | 3000 | 3000 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 6016.7527 |  | 85810.1664 | 241341.093 | 31617.3421 | 284556.0786 | 55936.7316 | 643324.6802 | 699261.4117 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -6876.2888 |  | -10514.9419 | -29573.2742 | -3874.3022 | 5778.2426 | -19140.2821 | -38184.2757 | -57324.5578
146 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.4803 | 2350 | 2350 | 14 | 6 | C | 4.5 | 6 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 3319.5877 |  | 85810.1664 | 241341.093 | 17444.0508 | 156996.4572 | 51671.2008 | 501591.7674 | 553262.9683 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -3793.8145 |  | -10514.9419 | -29573.2742 | -2137.546 | 3187.9959 | -14258.4657 | -39037.7663 | -53296.232
147 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 5.8907 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 2614.1753 |  | 85810.1664 | 241341.093 | 13737.19 | 123634.71 | 50460.9893 | 464523.1595 | 514984.1488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -2987.6289 |  | -10514.9419 | -29573.2742 | -1683.3175 | 2510.5468 | -12873.5559 | -39260.9869 | -52134.5428
148 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.3297 | 2125 | 2125 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2365.2062 |  | 85810.1664 | 241341.093 | 12428.8862 | 111859.9757 | 50013.1844 | 451440.1214 | 501453.3058 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -2703.0928 |  | -10514.9419 | -29573.2742 | -1523.0016 | 2271.4471 | -12361.1398 | -39339.7706 | -51700.9104
149 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 5.9219 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 2628.0069 |  | 85810.1664 | 241341.093 | 13809.8735 | 124288.8619 | 50476.1058 | 465249.9949 | 515726.1008 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3003.4365 |  | -10514.9419 | -29573.2742 | -1692.2239 | 2523.8301 | -12890.8675 | -39256.61 | -52147.4775
150 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 7.8855 | 2400 | 2400 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 3499.3987 |  | 85810.1664 | 241341.093 | 18388.9369 | 165500.4319 | 51955.5695 | 511040.6283 | 562996.1978 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -3999.3128 |  | -10514.9419 | -29573.2742 | -2253.3298 | 3360.679 | -14583.9201 | -38980.8669 | -53564.787
151 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.5997 | 2575 | 2575 | 16 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 4260.1375 |  | 85810.1664 | 241341.093 | 22386.5319 | 201478.7867 | 53226.2474 | 551016.578 | 604242.8254 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -4868.7286 |  | -10514.9419 | -29573.2742 | -2743.1841 | 4091.2614 | -16038.0763 | -38740.1388 | -54778.2151
152 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.4724 | 2675 | 2675 | 16 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 4647.4228 |  | 85810.1664 | 241341.093 | 24421.6711 | 219795.0401 | 53825.2179 | 571367.9706 | 625193.1886 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -5311.3403 |  | -10514.9419 | -29573.2742 | -2992.5645 | 4463.1943 | -16723.6083 | -38617.5863 | -55341.1947
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 165.7043 | 42375 | 42375 | 260 | 108.5 |  | 76.5 | 108.5
Zoning Area AHU - 10 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
153 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
154 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.0256 | 2850 | 2850 | 18 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 3 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 6224.2269 |  | 42905.0832 | 241341.093 | 32707.5952 | 294368.3572 | 48028.4934 | 611322.1287 | 659350.6222 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -7113.4022 |  | -5257.471 | -29573.2742 | -4007.8988 | 5977.4923 | -2791.3997 | -32861.1517 | -35652.5513
155 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.1712 | 2200 | 2200 | 14 | 5.5 | C | 4.5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 2738.6598 |  | 85810.1664 | 241341.093 | 14391.3419 | 129522.0772 | 50684.8917 | 471064.6785 | 521749.5702 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3129.897 |  | -10514.9419 | -29573.2742 | -1763.4755 | 2630.0966 | -13129.7639 | -39221.595 | -52351.3589
156 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.5453 | 2250 | 2250 | 14 | 6 | C | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 2904.6392 |  | 85810.1664 | 241341.093 | 15263.5444 | 137371.9 | 57953.8503 | 479786.7039 | 537740.5543 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -3319.5877 |  | -10514.9419 | -29573.2742 | -1870.3528 | 2789.4964 | -6814.7142 | -39169.0725 | -45983.7867
157 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.4542 | 2375 | 2375 | 14 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 5083.1186 |  | 0 | 241341.093 | 26711.2028 | 240400.8251 | 31383.123 | 508453.1209 | 539836.2439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -5809.2785 |  | 0 | -29573.2742 | -3273.1174 | 4881.6187 | 8923.3816 | -27964.7728 | -19041.3912
158 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 16.8307 | 3375 | 3375 | 20 | 8.5 | C | 5 | 8.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 7469.0723 |  | 85810.1664 | 241341.093 | 39249.1143 | 353242.0287 | 58226.7979 | 719642.4024 | 777869.2003 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -8536.0826 |  | -10514.9419 | -29573.2742 | -4809.4786 | 7172.9908 | -21761.229 | -37724.7039 | -59485.933
159 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 24.872 | 4450 | 4450 | 26 | 11.5 | C | 7 | 11.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 11037.6291 |  | 128715.2496 | 241341.093 | 58001.4689 | 522013.2201 | 81727.8063 | 950071.0317 | 1031798.838 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -12614.4332 |  | -15772.4129 | -29573.2742 | -7107.3406 | 10600.0864 | -34005.8283 | -41852.9413 | -75858.7696
160 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.5607 | 2900 | 2900 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 5574.141 |  | 85810.1664 | 241341.093 | 29291.4686 | 263623.2177 | 55277.2947 | 620065.9458 | 675343.2405 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -6370.4468 |  | -10514.9419 | -29573.2742 | -3589.2961 | 5353.1765 | -18385.5037 | -38324.3357 | -56709.8394
161 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.1063 | 2500 | 2500 | 16 | 6.5 | C | 6 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3153.6083 |  | 128715.2496 | 241341.093 | 16571.8483 | 149146.6343 | 66448.7887 | 535774.8253 | 602223.6139 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -3604.1238 |  | -15772.4129 | -29573.2742 | -2030.6687 | 3028.5961 | -23835.2829 | -44347.7597 | -68183.0426
162 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 13.558 | 3000 | 3000 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 6016.7527 |  | 85810.1664 | 241341.093 | 31617.3421 | 284556.0786 | 55936.7316 | 643324.6802 | 699261.4117 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -6876.2888 |  | -10514.9419 | -29573.2742 | -3874.3022 | 5778.2426 | -19140.2821 | -38184.2757 | -57324.5578
163 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.4803 | 2350 | 2350 | 14 | 6 | C | 4.5 | 6 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 3319.5877 |  | 85810.1664 | 241341.093 | 17444.0508 | 156996.4572 | 51671.2008 | 501591.7674 | 553262.9683 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -3793.8145 |  | -10514.9419 | -29573.2742 | -2137.546 | 3187.9959 | -14258.4657 | -39037.7663 | -53296.232
164 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 5.8907 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 2614.1753 |  | 85810.1664 | 241341.093 | 13737.19 | 123634.71 | 50460.9893 | 464523.1595 | 514984.1488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -2987.6289 |  | -10514.9419 | -29573.2742 | -1683.3175 | 2510.5468 | -12873.5559 | -39260.9869 | -52134.5428
165 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.3297 | 2125 | 2125 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2365.2062 |  | 85810.1664 | 241341.093 | 12428.8862 | 111859.9757 | 50013.1844 | 451440.1214 | 501453.3058 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -2703.0928 |  | -10514.9419 | -29573.2742 | -1523.0016 | 2271.4471 | -12361.1398 | -39339.7706 | -51700.9104
166 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 5.9219 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 2628.0069 |  | 85810.1664 | 241341.093 | 13809.8735 | 124288.8619 | 50476.1058 | 465249.9949 | 515726.1008 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3003.4365 |  | -10514.9419 | -29573.2742 | -1692.2239 | 2523.8301 | -12890.8675 | -39256.61 | -52147.4775
167 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 7.8855 | 2400 | 2400 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 3499.3987 |  | 85810.1664 | 241341.093 | 18388.9369 | 165500.4319 | 51955.5695 | 511040.6283 | 562996.1978 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -3999.3128 |  | -10514.9419 | -29573.2742 | -2253.3298 | 3360.679 | -14583.9201 | -38980.8669 | -53564.787
168 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.5997 | 2575 | 2575 | 16 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 4260.1375 |  | 85810.1664 | 241341.093 | 22386.5319 | 201478.7867 | 53226.2474 | 551016.578 | 604242.8254 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -4868.7286 |  | -10514.9419 | -29573.2742 | -2743.1841 | 4091.2614 | -16038.0763 | -38740.1388 | -54778.2151
169 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.4724 | 2675 | 2675 | 16 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 4647.4228 |  | 85810.1664 | 241341.093 | 24421.6711 | 219795.0401 | 53825.2179 | 571367.9706 | 625193.1886 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -5311.3403 |  | -10514.9419 | -29573.2742 | -2992.5645 | 4463.1943 | -16723.6083 | -38617.5863 | -55341.1947
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 165.7043 | 42375 | 42375 | 260 | 108.5 |  | 76.5 | 108.5
Zoning Area AHU - 11 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
170 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
171 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.0256 | 2850 | 2850 | 18 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 3 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 6224.2269 |  | 42905.0832 | 241341.093 | 32707.5952 | 294368.3572 | 48028.4934 | 611322.1287 | 659350.6222 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -7113.4022 |  | -5257.471 | -29573.2742 | -4007.8988 | 5977.4923 | -2791.3997 | -32861.1517 | -35652.5513
172 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.1712 | 2200 | 2200 | 14 | 5.5 | C | 4.5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 2738.6598 |  | 85810.1664 | 241341.093 | 14391.3419 | 129522.0772 | 50684.8917 | 471064.6785 | 521749.5702 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3129.897 |  | -10514.9419 | -29573.2742 | -1763.4755 | 2630.0966 | -13129.7639 | -39221.595 | -52351.3589
173 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.5453 | 2250 | 2250 | 14 | 6 | C | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 2904.6392 |  | 85810.1664 | 241341.093 | 15263.5444 | 137371.9 | 57953.8503 | 479786.7039 | 537740.5543 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -3319.5877 |  | -10514.9419 | -29573.2742 | -1870.3528 | 2789.4964 | -6814.7142 | -39169.0725 | -45983.7867
174 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.4542 | 2375 | 2375 | 14 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 5083.1186 |  | 0 | 241341.093 | 26711.2028 | 240400.8251 | 31383.123 | 508453.1209 | 539836.2439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -5809.2785 |  | 0 | -29573.2742 | -3273.1174 | 4881.6187 | 8923.3816 | -27964.7728 | -19041.3912
175 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 16.8307 | 3375 | 3375 | 20 | 8.5 | C | 5 | 8.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 7469.0723 |  | 85810.1664 | 241341.093 | 39249.1143 | 353242.0287 | 58226.7979 | 719642.4024 | 777869.2003 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -8536.0826 |  | -10514.9419 | -29573.2742 | -4809.4786 | 7172.9908 | -21761.229 | -37724.7039 | -59485.933
176 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 24.872 | 4450 | 4450 | 26 | 11.5 | C | 7 | 11.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 11037.6291 |  | 128715.2496 | 241341.093 | 58001.4689 | 522013.2201 | 81727.8063 | 950071.0317 | 1031798.838 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -12614.4332 |  | -15772.4129 | -29573.2742 | -7107.3406 | 10600.0864 | -34005.8283 | -41852.9413 | -75858.7696
177 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.5607 | 2900 | 2900 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 5574.141 |  | 85810.1664 | 241341.093 | 29291.4686 | 263623.2177 | 55277.2947 | 620065.9458 | 675343.2405 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -6370.4468 |  | -10514.9419 | -29573.2742 | -3589.2961 | 5353.1765 | -18385.5037 | -38324.3357 | -56709.8394
178 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.1063 | 2500 | 2500 | 16 | 6.5 | C | 6 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3153.6083 |  | 128715.2496 | 241341.093 | 16571.8483 | 149146.6343 | 66448.7887 | 535774.8253 | 602223.6139 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -3604.1238 |  | -15772.4129 | -29573.2742 | -2030.6687 | 3028.5961 | -23835.2829 | -44347.7597 | -68183.0426
179 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 13.558 | 3000 | 3000 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 6016.7527 |  | 85810.1664 | 241341.093 | 31617.3421 | 284556.0786 | 55936.7316 | 643324.6802 | 699261.4117 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -6876.2888 |  | -10514.9419 | -29573.2742 | -3874.3022 | 5778.2426 | -19140.2821 | -38184.2757 | -57324.5578
180 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.4803 | 2350 | 2350 | 14 | 6 | C | 4.5 | 6 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 3319.5877 |  | 85810.1664 | 241341.093 | 17444.0508 | 156996.4572 | 51671.2008 | 501591.7674 | 553262.9683 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -3793.8145 |  | -10514.9419 | -29573.2742 | -2137.546 | 3187.9959 | -14258.4657 | -39037.7663 | -53296.232
181 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 5.8907 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 2614.1753 |  | 85810.1664 | 241341.093 | 13737.19 | 123634.71 | 50460.9893 | 464523.1595 | 514984.1488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -2987.6289 |  | -10514.9419 | -29573.2742 | -1683.3175 | 2510.5468 | -12873.5559 | -39260.9869 | -52134.5428
182 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.3297 | 2125 | 2125 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2365.2062 |  | 85810.1664 | 241341.093 | 12428.8862 | 111859.9757 | 50013.1844 | 451440.1214 | 501453.3058 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -2703.0928 |  | -10514.9419 | -29573.2742 | -1523.0016 | 2271.4471 | -12361.1398 | -39339.7706 | -51700.9104
183 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 5.9219 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 2628.0069 |  | 85810.1664 | 241341.093 | 13809.8735 | 124288.8619 | 50476.1058 | 465249.9949 | 515726.1008 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3003.4365 |  | -10514.9419 | -29573.2742 | -1692.2239 | 2523.8301 | -12890.8675 | -39256.61 | -52147.4775
184 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 7.8855 | 2400 | 2400 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 3499.3987 |  | 85810.1664 | 241341.093 | 18388.9369 | 165500.4319 | 51955.5695 | 511040.6283 | 562996.1978 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -3999.3128 |  | -10514.9419 | -29573.2742 | -2253.3298 | 3360.679 | -14583.9201 | -38980.8669 | -53564.787
185 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.5997 | 2575 | 2575 | 16 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 4260.1375 |  | 85810.1664 | 241341.093 | 22386.5319 | 201478.7867 | 53226.2474 | 551016.578 | 604242.8254 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -4868.7286 |  | -10514.9419 | -29573.2742 | -2743.1841 | 4091.2614 | -16038.0763 | -38740.1388 | -54778.2151
186 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.4724 | 2675 | 2675 | 16 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 4647.4228 |  | 85810.1664 | 241341.093 | 24421.6711 | 219795.0401 | 53825.2179 | 571367.9706 | 625193.1886 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -5311.3403 |  | -10514.9419 | -29573.2742 | -2992.5645 | 4463.1943 | -16723.6083 | -38617.5863 | -55341.1947
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 165.7043 | 42375 | 42375 | 260 | 108.5 |  | 76.5 | 108.5
Zoning Area AHU - 12 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
187 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
188 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.0256 | 2850 | 2850 | 18 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 3 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 6224.2269 |  | 42905.0832 | 241341.093 | 32707.5952 | 294368.3572 | 48028.4934 | 611322.1287 | 659350.6222 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -7113.4022 |  | -5257.471 | -29573.2742 | -4007.8988 | 5977.4923 | -2791.3997 | -32861.1517 | -35652.5513
189 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.1712 | 2200 | 2200 | 14 | 5.5 | C | 4.5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 2738.6598 |  | 85810.1664 | 241341.093 | 14391.3419 | 129522.0772 | 50684.8917 | 471064.6785 | 521749.5702 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3129.897 |  | -10514.9419 | -29573.2742 | -1763.4755 | 2630.0966 | -13129.7639 | -39221.595 | -52351.3589
190 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.5453 | 2250 | 2250 | 14 | 6 | C | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 2904.6392 |  | 85810.1664 | 241341.093 | 15263.5444 | 137371.9 | 57953.8503 | 479786.7039 | 537740.5543 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -3319.5877 |  | -10514.9419 | -29573.2742 | -1870.3528 | 2789.4964 | -6814.7142 | -39169.0725 | -45983.7867
191 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.4542 | 2375 | 2375 | 14 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 5083.1186 |  | 0 | 241341.093 | 26711.2028 | 240400.8251 | 31383.123 | 508453.1209 | 539836.2439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -5809.2785 |  | 0 | -29573.2742 | -3273.1174 | 4881.6187 | 8923.3816 | -27964.7728 | -19041.3912
192 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 16.8307 | 3375 | 3375 | 20 | 8.5 | C | 5 | 8.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 7469.0723 |  | 85810.1664 | 241341.093 | 39249.1143 | 353242.0287 | 58226.7979 | 719642.4024 | 777869.2003 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -8536.0826 |  | -10514.9419 | -29573.2742 | -4809.4786 | 7172.9908 | -21761.229 | -37724.7039 | -59485.933
193 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 24.872 | 4450 | 4450 | 26 | 11.5 | C | 7 | 11.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 11037.6291 |  | 128715.2496 | 241341.093 | 58001.4689 | 522013.2201 | 81727.8063 | 950071.0317 | 1031798.838 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -12614.4332 |  | -15772.4129 | -29573.2742 | -7107.3406 | 10600.0864 | -34005.8283 | -41852.9413 | -75858.7696
194 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.5607 | 2900 | 2900 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 5574.141 |  | 85810.1664 | 241341.093 | 29291.4686 | 263623.2177 | 55277.2947 | 620065.9458 | 675343.2405 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -6370.4468 |  | -10514.9419 | -29573.2742 | -3589.2961 | 5353.1765 | -18385.5037 | -38324.3357 | -56709.8394
195 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.1063 | 2500 | 2500 | 16 | 6.5 | C | 6 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3153.6083 |  | 128715.2496 | 241341.093 | 16571.8483 | 149146.6343 | 66448.7887 | 535774.8253 | 602223.6139 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -3604.1238 |  | -15772.4129 | -29573.2742 | -2030.6687 | 3028.5961 | -23835.2829 | -44347.7597 | -68183.0426
196 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 13.558 | 3000 | 3000 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 6016.7527 |  | 85810.1664 | 241341.093 | 31617.3421 | 284556.0786 | 55936.7316 | 643324.6802 | 699261.4117 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -6876.2888 |  | -10514.9419 | -29573.2742 | -3874.3022 | 5778.2426 | -19140.2821 | -38184.2757 | -57324.5578
197 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.4803 | 2350 | 2350 | 14 | 6 | C | 4.5 | 6 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 3319.5877 |  | 85810.1664 | 241341.093 | 17444.0508 | 156996.4572 | 51671.2008 | 501591.7674 | 553262.9683 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -3793.8145 |  | -10514.9419 | -29573.2742 | -2137.546 | 3187.9959 | -14258.4657 | -39037.7663 | -53296.232
198 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 5.8907 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 2614.1753 |  | 85810.1664 | 241341.093 | 13737.19 | 123634.71 | 50460.9893 | 464523.1595 | 514984.1488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -2987.6289 |  | -10514.9419 | -29573.2742 | -1683.3175 | 2510.5468 | -12873.5559 | -39260.9869 | -52134.5428
199 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.3297 | 2125 | 2125 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2365.2062 |  | 85810.1664 | 241341.093 | 12428.8862 | 111859.9757 | 50013.1844 | 451440.1214 | 501453.3058 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -2703.0928 |  | -10514.9419 | -29573.2742 | -1523.0016 | 2271.4471 | -12361.1398 | -39339.7706 | -51700.9104
200 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 5.9219 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 2628.0069 |  | 85810.1664 | 241341.093 | 13809.8735 | 124288.8619 | 50476.1058 | 465249.9949 | 515726.1008 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3003.4365 |  | -10514.9419 | -29573.2742 | -1692.2239 | 2523.8301 | -12890.8675 | -39256.61 | -52147.4775
201 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 7.8855 | 2400 | 2400 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 3499.3987 |  | 85810.1664 | 241341.093 | 18388.9369 | 165500.4319 | 51955.5695 | 511040.6283 | 562996.1978 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -3999.3128 |  | -10514.9419 | -29573.2742 | -2253.3298 | 3360.679 | -14583.9201 | -38980.8669 | -53564.787
202 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.5997 | 2575 | 2575 | 16 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 4260.1375 |  | 85810.1664 | 241341.093 | 22386.5319 | 201478.7867 | 53226.2474 | 551016.578 | 604242.8254 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -4868.7286 |  | -10514.9419 | -29573.2742 | -2743.1841 | 4091.2614 | -16038.0763 | -38740.1388 | -54778.2151
203 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.4724 | 2675 | 2675 | 16 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 4647.4228 |  | 85810.1664 | 241341.093 | 24421.6711 | 219795.0401 | 53825.2179 | 571367.9706 | 625193.1886 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -5311.3403 |  | -10514.9419 | -29573.2742 | -2992.5645 | 4463.1943 | -16723.6083 | -38617.5863 | -55341.1947
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 165.7043 | 42375 | 42375 | 260 | 108.5 |  | 76.5 | 108.5
Zoning Area AHU - 13 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
204 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
205 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.0256 | 2850 | 2850 | 18 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 3 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 6224.2269 |  | 42905.0832 | 241341.093 | 32707.5952 | 294368.3572 | 48028.4934 | 611322.1287 | 659350.6222 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -7113.4022 |  | -5257.471 | -29573.2742 | -4007.8988 | 5977.4923 | -2791.3997 | -32861.1517 | -35652.5513
206 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.1712 | 2200 | 2200 | 14 | 5.5 | C | 4.5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 2738.6598 |  | 85810.1664 | 241341.093 | 14391.3419 | 129522.0772 | 50684.8917 | 471064.6785 | 521749.5702 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3129.897 |  | -10514.9419 | -29573.2742 | -1763.4755 | 2630.0966 | -13129.7639 | -39221.595 | -52351.3589
207 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.5453 | 2250 | 2250 | 14 | 6 | C | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 2904.6392 |  | 85810.1664 | 241341.093 | 15263.5444 | 137371.9 | 57953.8503 | 479786.7039 | 537740.5543 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -3319.5877 |  | -10514.9419 | -29573.2742 | -1870.3528 | 2789.4964 | -6814.7142 | -39169.0725 | -45983.7867
208 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.4542 | 2375 | 2375 | 14 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 5083.1186 |  | 0 | 241341.093 | 26711.2028 | 240400.8251 | 31383.123 | 508453.1209 | 539836.2439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -5809.2785 |  | 0 | -29573.2742 | -3273.1174 | 4881.6187 | 8923.3816 | -27964.7728 | -19041.3912
209 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 16.8307 | 3375 | 3375 | 20 | 8.5 | C | 5 | 8.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 7469.0723 |  | 85810.1664 | 241341.093 | 39249.1143 | 353242.0287 | 58226.7979 | 719642.4024 | 777869.2003 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -8536.0826 |  | -10514.9419 | -29573.2742 | -4809.4786 | 7172.9908 | -21761.229 | -37724.7039 | -59485.933
210 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 24.872 | 4450 | 4450 | 26 | 11.5 | C | 7 | 11.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 11037.6291 |  | 128715.2496 | 241341.093 | 58001.4689 | 522013.2201 | 81727.8063 | 950071.0317 | 1031798.838 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -12614.4332 |  | -15772.4129 | -29573.2742 | -7107.3406 | 10600.0864 | -34005.8283 | -41852.9413 | -75858.7696
211 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.5607 | 2900 | 2900 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 5574.141 |  | 85810.1664 | 241341.093 | 29291.4686 | 263623.2177 | 55277.2947 | 620065.9458 | 675343.2405 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -6370.4468 |  | -10514.9419 | -29573.2742 | -3589.2961 | 5353.1765 | -18385.5037 | -38324.3357 | -56709.8394
212 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.1063 | 2500 | 2500 | 16 | 6.5 | C | 6 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3153.6083 |  | 128715.2496 | 241341.093 | 16571.8483 | 149146.6343 | 66448.7887 | 535774.8253 | 602223.6139 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -3604.1238 |  | -15772.4129 | -29573.2742 | -2030.6687 | 3028.5961 | -23835.2829 | -44347.7597 | -68183.0426
213 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 13.558 | 3000 | 3000 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 6016.7527 |  | 85810.1664 | 241341.093 | 31617.3421 | 284556.0786 | 55936.7316 | 643324.6802 | 699261.4117 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -6876.2888 |  | -10514.9419 | -29573.2742 | -3874.3022 | 5778.2426 | -19140.2821 | -38184.2757 | -57324.5578
214 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.4803 | 2350 | 2350 | 14 | 6 | C | 4.5 | 6 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 3319.5877 |  | 85810.1664 | 241341.093 | 17444.0508 | 156996.4572 | 51671.2008 | 501591.7674 | 553262.9683 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -3793.8145 |  | -10514.9419 | -29573.2742 | -2137.546 | 3187.9959 | -14258.4657 | -39037.7663 | -53296.232
215 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 5.8907 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 2614.1753 |  | 85810.1664 | 241341.093 | 13737.19 | 123634.71 | 50460.9893 | 464523.1595 | 514984.1488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -2987.6289 |  | -10514.9419 | -29573.2742 | -1683.3175 | 2510.5468 | -12873.5559 | -39260.9869 | -52134.5428
216 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.3297 | 2125 | 2125 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2365.2062 |  | 85810.1664 | 241341.093 | 12428.8862 | 111859.9757 | 50013.1844 | 451440.1214 | 501453.3058 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -2703.0928 |  | -10514.9419 | -29573.2742 | -1523.0016 | 2271.4471 | -12361.1398 | -39339.7706 | -51700.9104
217 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 5.9219 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 2628.0069 |  | 85810.1664 | 241341.093 | 13809.8735 | 124288.8619 | 50476.1058 | 465249.9949 | 515726.1008 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3003.4365 |  | -10514.9419 | -29573.2742 | -1692.2239 | 2523.8301 | -12890.8675 | -39256.61 | -52147.4775
218 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 7.8855 | 2400 | 2400 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 3499.3987 |  | 85810.1664 | 241341.093 | 18388.9369 | 165500.4319 | 51955.5695 | 511040.6283 | 562996.1978 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -3999.3128 |  | -10514.9419 | -29573.2742 | -2253.3298 | 3360.679 | -14583.9201 | -38980.8669 | -53564.787
219 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.5997 | 2575 | 2575 | 16 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 4260.1375 |  | 85810.1664 | 241341.093 | 22386.5319 | 201478.7867 | 53226.2474 | 551016.578 | 604242.8254 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -4868.7286 |  | -10514.9419 | -29573.2742 | -2743.1841 | 4091.2614 | -16038.0763 | -38740.1388 | -54778.2151
220 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.4724 | 2675 | 2675 | 16 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 4647.4228 |  | 85810.1664 | 241341.093 | 24421.6711 | 219795.0401 | 53825.2179 | 571367.9706 | 625193.1886 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -5311.3403 |  | -10514.9419 | -29573.2742 | -2992.5645 | 4463.1943 | -16723.6083 | -38617.5863 | -55341.1947
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 165.7043 | 42375 | 42375 | 260 | 108.5 |  | 76.5 | 108.5
Zoning Area AHU - 14 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
221 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
222 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.0256 | 2850 | 2850 | 18 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 3 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 6224.2269 |  | 42905.0832 | 241341.093 | 32707.5952 | 294368.3572 | 48028.4934 | 611322.1287 | 659350.6222 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -7113.4022 |  | -5257.471 | -29573.2742 | -4007.8988 | 5977.4923 | -2791.3997 | -32861.1517 | -35652.5513
223 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.1712 | 2200 | 2200 | 14 | 5.5 | C | 4.5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 2738.6598 |  | 85810.1664 | 241341.093 | 14391.3419 | 129522.0772 | 50684.8917 | 471064.6785 | 521749.5702 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3129.897 |  | -10514.9419 | -29573.2742 | -1763.4755 | 2630.0966 | -13129.7639 | -39221.595 | -52351.3589
224 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.5453 | 2250 | 2250 | 14 | 6 | C | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 2904.6392 |  | 85810.1664 | 241341.093 | 15263.5444 | 137371.9 | 57953.8503 | 479786.7039 | 537740.5543 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -3319.5877 |  | -10514.9419 | -29573.2742 | -1870.3528 | 2789.4964 | -6814.7142 | -39169.0725 | -45983.7867
225 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.4542 | 2375 | 2375 | 14 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 5083.1186 |  | 0 | 241341.093 | 26711.2028 | 240400.8251 | 31383.123 | 508453.1209 | 539836.2439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -5809.2785 |  | 0 | -29573.2742 | -3273.1174 | 4881.6187 | 8923.3816 | -27964.7728 | -19041.3912
226 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 16.8307 | 3375 | 3375 | 20 | 8.5 | C | 5 | 8.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 7469.0723 |  | 85810.1664 | 241341.093 | 39249.1143 | 353242.0287 | 58226.7979 | 719642.4024 | 777869.2003 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -8536.0826 |  | -10514.9419 | -29573.2742 | -4809.4786 | 7172.9908 | -21761.229 | -37724.7039 | -59485.933
227 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 24.872 | 4450 | 4450 | 26 | 11.5 | C | 7 | 11.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 11037.6291 |  | 128715.2496 | 241341.093 | 58001.4689 | 522013.2201 | 81727.8063 | 950071.0317 | 1031798.838 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -12614.4332 |  | -15772.4129 | -29573.2742 | -7107.3406 | 10600.0864 | -34005.8283 | -41852.9413 | -75858.7696
228 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.5607 | 2900 | 2900 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 5574.141 |  | 85810.1664 | 241341.093 | 29291.4686 | 263623.2177 | 55277.2947 | 620065.9458 | 675343.2405 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -6370.4468 |  | -10514.9419 | -29573.2742 | -3589.2961 | 5353.1765 | -18385.5037 | -38324.3357 | -56709.8394
229 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.1063 | 2500 | 2500 | 16 | 6.5 | C | 6 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3153.6083 |  | 128715.2496 | 241341.093 | 16571.8483 | 149146.6343 | 66448.7887 | 535774.8253 | 602223.6139 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -3604.1238 |  | -15772.4129 | -29573.2742 | -2030.6687 | 3028.5961 | -23835.2829 | -44347.7597 | -68183.0426
230 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 13.558 | 3000 | 3000 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 6016.7527 |  | 85810.1664 | 241341.093 | 31617.3421 | 284556.0786 | 55936.7316 | 643324.6802 | 699261.4117 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -6876.2888 |  | -10514.9419 | -29573.2742 | -3874.3022 | 5778.2426 | -19140.2821 | -38184.2757 | -57324.5578
231 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.4803 | 2350 | 2350 | 14 | 6 | C | 4.5 | 6 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 3319.5877 |  | 85810.1664 | 241341.093 | 17444.0508 | 156996.4572 | 51671.2008 | 501591.7674 | 553262.9683 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -3793.8145 |  | -10514.9419 | -29573.2742 | -2137.546 | 3187.9959 | -14258.4657 | -39037.7663 | -53296.232
232 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 5.8907 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 2614.1753 |  | 85810.1664 | 241341.093 | 13737.19 | 123634.71 | 50460.9893 | 464523.1595 | 514984.1488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -2987.6289 |  | -10514.9419 | -29573.2742 | -1683.3175 | 2510.5468 | -12873.5559 | -39260.9869 | -52134.5428
233 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.3297 | 2125 | 2125 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2365.2062 |  | 85810.1664 | 241341.093 | 12428.8862 | 111859.9757 | 50013.1844 | 451440.1214 | 501453.3058 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -2703.0928 |  | -10514.9419 | -29573.2742 | -1523.0016 | 2271.4471 | -12361.1398 | -39339.7706 | -51700.9104
234 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 5.9219 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 2628.0069 |  | 85810.1664 | 241341.093 | 13809.8735 | 124288.8619 | 50476.1058 | 465249.9949 | 515726.1008 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3003.4365 |  | -10514.9419 | -29573.2742 | -1692.2239 | 2523.8301 | -12890.8675 | -39256.61 | -52147.4775
235 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 7.8855 | 2400 | 2400 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 3499.3987 |  | 85810.1664 | 241341.093 | 18388.9369 | 165500.4319 | 51955.5695 | 511040.6283 | 562996.1978 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -3999.3128 |  | -10514.9419 | -29573.2742 | -2253.3298 | 3360.679 | -14583.9201 | -38980.8669 | -53564.787
236 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.5997 | 2575 | 2575 | 16 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 4260.1375 |  | 85810.1664 | 241341.093 | 22386.5319 | 201478.7867 | 53226.2474 | 551016.578 | 604242.8254 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -4868.7286 |  | -10514.9419 | -29573.2742 | -2743.1841 | 4091.2614 | -16038.0763 | -38740.1388 | -54778.2151
237 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.4724 | 2675 | 2675 | 16 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 4647.4228 |  | 85810.1664 | 241341.093 | 24421.6711 | 219795.0401 | 53825.2179 | 571367.9706 | 625193.1886 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -5311.3403 |  | -10514.9419 | -29573.2742 | -2992.5645 | 4463.1943 | -16723.6083 | -38617.5863 | -55341.1947
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 165.7043 | 42375 | 42375 | 260 | 108.5 |  | 76.5 | 108.5
Zoning Area AHU - 15 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
238 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
239 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.0256 | 2850 | 2850 | 18 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 3 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 6224.2269 |  | 42905.0832 | 241341.093 | 32707.5952 | 294368.3572 | 48028.4934 | 611322.1287 | 659350.6222 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -7113.4022 |  | -5257.471 | -29573.2742 | -4007.8988 | 5977.4923 | -2791.3997 | -32861.1517 | -35652.5513
240 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.1712 | 2200 | 2200 | 14 | 5.5 | C | 4.5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 2738.6598 |  | 85810.1664 | 241341.093 | 14391.3419 | 129522.0772 | 50684.8917 | 471064.6785 | 521749.5702 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3129.897 |  | -10514.9419 | -29573.2742 | -1763.4755 | 2630.0966 | -13129.7639 | -39221.595 | -52351.3589
241 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.5453 | 2250 | 2250 | 14 | 6 | C | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 2904.6392 |  | 85810.1664 | 241341.093 | 15263.5444 | 137371.9 | 57953.8503 | 479786.7039 | 537740.5543 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -3319.5877 |  | -10514.9419 | -29573.2742 | -1870.3528 | 2789.4964 | -6814.7142 | -39169.0725 | -45983.7867
242 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.4542 | 2375 | 2375 | 14 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 5083.1186 |  | 0 | 241341.093 | 26711.2028 | 240400.8251 | 31383.123 | 508453.1209 | 539836.2439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -5809.2785 |  | 0 | -29573.2742 | -3273.1174 | 4881.6187 | 8923.3816 | -27964.7728 | -19041.3912
243 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 16.8307 | 3375 | 3375 | 20 | 8.5 | C | 5 | 8.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 7469.0723 |  | 85810.1664 | 241341.093 | 39249.1143 | 353242.0287 | 58226.7979 | 719642.4024 | 777869.2003 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -8536.0826 |  | -10514.9419 | -29573.2742 | -4809.4786 | 7172.9908 | -21761.229 | -37724.7039 | -59485.933
244 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 24.872 | 4450 | 4450 | 26 | 11.5 | C | 7 | 11.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 11037.6291 |  | 128715.2496 | 241341.093 | 58001.4689 | 522013.2201 | 81727.8063 | 950071.0317 | 1031798.838 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -12614.4332 |  | -15772.4129 | -29573.2742 | -7107.3406 | 10600.0864 | -34005.8283 | -41852.9413 | -75858.7696
245 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.5607 | 2900 | 2900 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 5574.141 |  | 85810.1664 | 241341.093 | 29291.4686 | 263623.2177 | 55277.2947 | 620065.9458 | 675343.2405 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -6370.4468 |  | -10514.9419 | -29573.2742 | -3589.2961 | 5353.1765 | -18385.5037 | -38324.3357 | -56709.8394
246 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.1063 | 2500 | 2500 | 16 | 6.5 | C | 6 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3153.6083 |  | 128715.2496 | 241341.093 | 16571.8483 | 149146.6343 | 66448.7887 | 535774.8253 | 602223.6139 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -3604.1238 |  | -15772.4129 | -29573.2742 | -2030.6687 | 3028.5961 | -23835.2829 | -44347.7597 | -68183.0426
247 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 13.558 | 3000 | 3000 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 6016.7527 |  | 85810.1664 | 241341.093 | 31617.3421 | 284556.0786 | 55936.7316 | 643324.6802 | 699261.4117 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -6876.2888 |  | -10514.9419 | -29573.2742 | -3874.3022 | 5778.2426 | -19140.2821 | -38184.2757 | -57324.5578
248 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.4803 | 2350 | 2350 | 14 | 6 | C | 4.5 | 6 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 3319.5877 |  | 85810.1664 | 241341.093 | 17444.0508 | 156996.4572 | 51671.2008 | 501591.7674 | 553262.9683 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -3793.8145 |  | -10514.9419 | -29573.2742 | -2137.546 | 3187.9959 | -14258.4657 | -39037.7663 | -53296.232
249 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 5.8907 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 2614.1753 |  | 85810.1664 | 241341.093 | 13737.19 | 123634.71 | 50460.9893 | 464523.1595 | 514984.1488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -2987.6289 |  | -10514.9419 | -29573.2742 | -1683.3175 | 2510.5468 | -12873.5559 | -39260.9869 | -52134.5428
250 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.3297 | 2125 | 2125 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2365.2062 |  | 85810.1664 | 241341.093 | 12428.8862 | 111859.9757 | 50013.1844 | 451440.1214 | 501453.3058 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -2703.0928 |  | -10514.9419 | -29573.2742 | -1523.0016 | 2271.4471 | -12361.1398 | -39339.7706 | -51700.9104
251 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 5.9219 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 2628.0069 |  | 85810.1664 | 241341.093 | 13809.8735 | 124288.8619 | 50476.1058 | 465249.9949 | 515726.1008 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3003.4365 |  | -10514.9419 | -29573.2742 | -1692.2239 | 2523.8301 | -12890.8675 | -39256.61 | -52147.4775
252 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 7.8855 | 2400 | 2400 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 3499.3987 |  | 85810.1664 | 241341.093 | 18388.9369 | 165500.4319 | 51955.5695 | 511040.6283 | 562996.1978 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -3999.3128 |  | -10514.9419 | -29573.2742 | -2253.3298 | 3360.679 | -14583.9201 | -38980.8669 | -53564.787
253 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.5997 | 2575 | 2575 | 16 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 4260.1375 |  | 85810.1664 | 241341.093 | 22386.5319 | 201478.7867 | 53226.2474 | 551016.578 | 604242.8254 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -4868.7286 |  | -10514.9419 | -29573.2742 | -2743.1841 | 4091.2614 | -16038.0763 | -38740.1388 | -54778.2151
254 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.4724 | 2675 | 2675 | 16 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 4647.4228 |  | 85810.1664 | 241341.093 | 24421.6711 | 219795.0401 | 53825.2179 | 571367.9706 | 625193.1886 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -5311.3403 |  | -10514.9419 | -29573.2742 | -2992.5645 | 4463.1943 | -16723.6083 | -38617.5863 | -55341.1947
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 165.7043 | 42375 | 42375 | 260 | 108.5 |  | 76.5 | 108.5
Zoning Area AHU - 16 Ventilation System | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
255 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
256 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 1524.649 | Ambient | Ambient | 1700 | 10 | Ambient | C | Ambient | Ambient | 20000 | W | 150 | 800 | 30 | Amb | 0 | 3 | 0 | 0 | 2 | 0 |  |  |  |  | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6824 | 578.2316 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6824 | 578.2316 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
257 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 670.8455 | Ambient | Ambient | 750 | 6 | Ambient | C | Ambient | Ambient |  | 2900 | [14 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 254.4219 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 254.4219 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
258 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 711.5028 | Ambient | Ambient | 800 | 6 | Ambient | C | Ambient | Ambient |  | H | [14 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 10236 | 269.8414 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 10236 | 269.8414 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
259 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 1245.13 | Ambient | Ambient | 1375 | 8 | Ambient | C | Ambient | Ambient |  | 2050 | [14 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 472.2225 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 472.2225 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
260 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 1829.5788 | Ambient | Ambient | 2025 | 12 | Ambient | C | Ambient | Ambient |  | L | [14 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 693.878 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 693.878 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
261 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 2703.7108 | Ambient | Ambient | 2975 | 18 | Ambient | C | Ambient | Ambient |  | 6400 | [14 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 10236 | 1025.3974 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 10236 | 1025.3974 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
262 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 1365.4078 | Ambient | Ambient | 1525 | 10 | Ambient | C | Ambient | Ambient | [16 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 517.8386 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 517.8386 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
263 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 772.4888 | Ambient | Ambient | 850 | 6 | Ambient | C | Ambient | Ambient | [16 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6824 | 292.9707 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6824 | 292.9707 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
264 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 1473.8273 | Ambient | Ambient | 1625 | 10 | Ambient | C | Ambient | Ambient | [16 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 558.9573 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 558.9573 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
265 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 813.1461 | Ambient | Ambient | 900 | 6 | Ambient | C | Ambient | Ambient |  | 6000 | [14 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 308.3902 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 308.3902 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
266 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 640.3526 | Ambient | Ambient | 725 | 6 | Ambient | C | Ambient | Ambient | [16 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 242.8573 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 242.8573 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
267 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 579.3666 | Ambient | Ambient | 650 | 4 | Ambient | C | Ambient | Ambient | [16 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 219.728 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 219.728 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
268 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 643.7407 | Ambient | Ambient | 725 | 6 | Ambient | C | Ambient | Ambient | [16 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 244.1422 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 244.1422 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
269 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 857.1915 | Ambient | Ambient | 950 | 6 | Ambient | C | Ambient | Ambient | [16 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 325.0947 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 325.0947 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
270 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 1043.5375 | Ambient | Ambient | 1150 | 8 | Ambient | C | Ambient | Ambient | [16 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 395.7674 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 395.7674 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
271 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | amb | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 1138.4046 | Ambient | Ambient | 1275 | 8 | Ambient | C | Ambient | Ambient | [16 empty] | #VALUE! | #VALUE! | #VALUE! | 85 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 45 | 85 | 380.5412 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 431.7463 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | #VALUE! | amb | 50 | #VALUE! | #VALUE! | 0 | 100 | 26.4048 | amb | 50 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3412 | 431.7463 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 18012.8804 | 0 | 0 | 20000 | 130 | 0 |  | 0 | 0
Zoning Area AHU - 17 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
272 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
273 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.0256 | 2850 | 2850 | 18 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 3 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 6224.2269 |  | 42905.0832 | 241341.093 | 32707.5952 | 294368.3572 | 48028.4934 | 611322.1287 | 659350.6222 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -7113.4022 |  | -5257.471 | -29573.2742 | -4007.8988 | 5977.4923 | -2791.3997 | -32861.1517 | -35652.5513
274 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.1712 | 2200 | 2200 | 14 | 5.5 | C | 4.5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 2738.6598 |  | 85810.1664 | 241341.093 | 14391.3419 | 129522.0772 | 50684.8917 | 471064.6785 | 521749.5702 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3129.897 |  | -10514.9419 | -29573.2742 | -1763.4755 | 2630.0966 | -13129.7639 | -39221.595 | -52351.3589
275 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.5453 | 2250 | 2250 | 14 | 6 | C | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 2904.6392 |  | 85810.1664 | 241341.093 | 15263.5444 | 137371.9 | 57953.8503 | 479786.7039 | 537740.5543 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -3319.5877 |  | -10514.9419 | -29573.2742 | -1870.3528 | 2789.4964 | -6814.7142 | -39169.0725 | -45983.7867
276 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.4542 | 2375 | 2375 | 14 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 5083.1186 |  | 0 | 241341.093 | 26711.2028 | 240400.8251 | 31383.123 | 508453.1209 | 539836.2439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -5809.2785 |  | 0 | -29573.2742 | -3273.1174 | 4881.6187 | 8923.3816 | -27964.7728 | -19041.3912
277 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 16.8307 | 3375 | 3375 | 20 | 8.5 | C | 5 | 8.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 7469.0723 |  | 85810.1664 | 241341.093 | 39249.1143 | 353242.0287 | 58226.7979 | 719642.4024 | 777869.2003 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -8536.0826 |  | -10514.9419 | -29573.2742 | -4809.4786 | 7172.9908 | -21761.229 | -37724.7039 | -59485.933
278 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 24.872 | 4450 | 4450 | 26 | 11.5 | C | 7 | 11.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 11037.6291 |  | 128715.2496 | 241341.093 | 58001.4689 | 522013.2201 | 81727.8063 | 950071.0317 | 1031798.838 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -12614.4332 |  | -15772.4129 | -29573.2742 | -7107.3406 | 10600.0864 | -34005.8283 | -41852.9413 | -75858.7696
279 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.5607 | 2900 | 2900 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 5574.141 |  | 85810.1664 | 241341.093 | 29291.4686 | 263623.2177 | 55277.2947 | 620065.9458 | 675343.2405 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -6370.4468 |  | -10514.9419 | -29573.2742 | -3589.2961 | 5353.1765 | -18385.5037 | -38324.3357 | -56709.8394
280 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.1063 | 2500 | 2500 | 16 | 6.5 | C | 6 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3153.6083 |  | 128715.2496 | 241341.093 | 16571.8483 | 149146.6343 | 66448.7887 | 535774.8253 | 602223.6139 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -3604.1238 |  | -15772.4129 | -29573.2742 | -2030.6687 | 3028.5961 | -23835.2829 | -44347.7597 | -68183.0426
281 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 13.558 | 3000 | 3000 | 18 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 6016.7527 |  | 85810.1664 | 241341.093 | 31617.3421 | 284556.0786 | 55936.7316 | 643324.6802 | 699261.4117 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -6876.2888 |  | -10514.9419 | -29573.2742 | -3874.3022 | 5778.2426 | -19140.2821 | -38184.2757 | -57324.5578
282 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.4803 | 2350 | 2350 | 14 | 6 | C | 4.5 | 6 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 3319.5877 |  | 85810.1664 | 241341.093 | 17444.0508 | 156996.4572 | 51671.2008 | 501591.7674 | 553262.9683 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -3793.8145 |  | -10514.9419 | -29573.2742 | -2137.546 | 3187.9959 | -14258.4657 | -39037.7663 | -53296.232
283 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 5.8907 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 2614.1753 |  | 85810.1664 | 241341.093 | 13737.19 | 123634.71 | 50460.9893 | 464523.1595 | 514984.1488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -2987.6289 |  | -10514.9419 | -29573.2742 | -1683.3175 | 2510.5468 | -12873.5559 | -39260.9869 | -52134.5428
284 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.3297 | 2125 | 2125 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2365.2062 |  | 85810.1664 | 241341.093 | 12428.8862 | 111859.9757 | 50013.1844 | 451440.1214 | 501453.3058 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -2703.0928 |  | -10514.9419 | -29573.2742 | -1523.0016 | 2271.4471 | -12361.1398 | -39339.7706 | -51700.9104
285 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 5.9219 | 2175 | 2175 | 14 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 2628.0069 |  | 85810.1664 | 241341.093 | 13809.8735 | 124288.8619 | 50476.1058 | 465249.9949 | 515726.1008 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3003.4365 |  | -10514.9419 | -29573.2742 | -1692.2239 | 2523.8301 | -12890.8675 | -39256.61 | -52147.4775
286 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 7.8855 | 2400 | 2400 | 14 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 3499.3987 |  | 85810.1664 | 241341.093 | 18388.9369 | 165500.4319 | 51955.5695 | 511040.6283 | 562996.1978 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -3999.3128 |  | -10514.9419 | -29573.2742 | -2253.3298 | 3360.679 | -14583.9201 | -38980.8669 | -53564.787
287 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.5997 | 2575 | 2575 | 16 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 4260.1375 |  | 85810.1664 | 241341.093 | 22386.5319 | 201478.7867 | 53226.2474 | 551016.578 | 604242.8254 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -4868.7286 |  | -10514.9419 | -29573.2742 | -2743.1841 | 4091.2614 | -16038.0763 | -38740.1388 | -54778.2151
288 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 6 | 120 | 0 | 100 | ISO 6 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.4724 | 2675 | 2675 | 16 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 4647.4228 |  | 85810.1664 | 241341.093 | 24421.6711 | 219795.0401 | 53825.2179 | 571367.9706 | 625193.1886 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -5311.3403 |  | -10514.9419 | -29573.2742 | -2992.5645 | 4463.1943 | -16723.6083 | -38617.5863 | -55341.1947
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 165.7043 | 42375 | 42375 | 260 | 108.5 |  | 76.5 | 108.5
Zoning Area AHU - 18 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
289 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
290 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.0256 | 2850 | 2850 | 30 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 4 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 6224.2269 |  | 42905.0832 | 241341.093 | 32707.5952 | 294368.3572 | 48028.4934 | 611322.1287 | 659350.6222 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -7113.4022 |  | -5257.471 | -29573.2742 | -4007.8988 | 5977.4923 | -2791.3997 | -32861.1517 | -35652.5513
291 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.1712 | 2200 | 2200 | 22 | 5.5 | C | 4.5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 2738.6598 |  | 85810.1664 | 241341.093 | 14391.3419 | 129522.0772 | 50684.8917 | 471064.6785 | 521749.5702 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3129.897 |  | -10514.9419 | -29573.2742 | -1763.4755 | 2630.0966 | -13129.7639 | -39221.595 | -52351.3589
292 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.5453 | 2250 | 2250 | 24 | 6 | C | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 2904.6392 |  | 85810.1664 | 241341.093 | 15263.5444 | 137371.9 | 57953.8503 | 479786.7039 | 537740.5543 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -3319.5877 |  | -10514.9419 | -29573.2742 | -1870.3528 | 2789.4964 | -6814.7142 | -39169.0725 | -45983.7867
293 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.4542 | 2375 | 2375 | 24 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 5083.1186 |  | 0 | 241341.093 | 26711.2028 | 240400.8251 | 31383.123 | 508453.1209 | 539836.2439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -5809.2785 |  | 0 | -29573.2742 | -3273.1174 | 4881.6187 | 8923.3816 | -27964.7728 | -19041.3912
294 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 16.8307 | 3375 | 3375 | 34 | 8.5 | C | 5 | 8.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 7469.0723 |  | 85810.1664 | 241341.093 | 39249.1143 | 353242.0287 | 58226.7979 | 719642.4024 | 777869.2003 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -8536.0826 |  | -10514.9419 | -29573.2742 | -4809.4786 | 7172.9908 | -21761.229 | -37724.7039 | -59485.933
295 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 24.872 | 4450 | 4450 | 46 | 11.5 | C | 7 | 11.5 |  | 6800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 11037.6291 |  | 128715.2496 | 241341.093 | 58001.4689 | 522013.2201 | 81727.8063 | 950071.0317 | 1031798.838 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -12614.4332 |  | -15772.4129 | -29573.2742 | -7107.3406 | 10600.0864 | -34005.8283 | -41852.9413 | -75858.7696
296 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.5607 | 2900 | 2900 | 30 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 5574.141 |  | 85810.1664 | 241341.093 | 29291.4686 | 263623.2177 | 55277.2947 | 620065.9458 | 675343.2405 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -6370.4468 |  | -10514.9419 | -29573.2742 | -3589.2961 | 5353.1765 | -18385.5037 | -38324.3357 | -56709.8394
297 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.1063 | 2500 | 2500 | 26 | 6.5 | C | 6 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3153.6083 |  | 128715.2496 | 241341.093 | 16571.8483 | 149146.6343 | 66448.7887 | 535774.8253 | 602223.6139 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -3604.1238 |  | -15772.4129 | -29573.2742 | -2030.6687 | 3028.5961 | -23835.2829 | -44347.7597 | -68183.0426
298 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 13.558 | 3000 | 3000 | 30 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 6016.7527 |  | 85810.1664 | 241341.093 | 31617.3421 | 284556.0786 | 55936.7316 | 643324.6802 | 699261.4117 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -6876.2888 |  | -10514.9419 | -29573.2742 | -3874.3022 | 5778.2426 | -19140.2821 | -38184.2757 | -57324.5578
299 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.4803 | 2350 | 2350 | 24 | 6 | C | 4.5 | 6 |  | 6400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 3319.5877 |  | 85810.1664 | 241341.093 | 17444.0508 | 156996.4572 | 51671.2008 | 501591.7674 | 553262.9683 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -3793.8145 |  | -10514.9419 | -29573.2742 | -2137.546 | 3187.9959 | -14258.4657 | -39037.7663 | -53296.232
300 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 5.8907 | 2175 | 2175 | 22 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 2614.1753 |  | 85810.1664 | 241341.093 | 13737.19 | 123634.71 | 50460.9893 | 464523.1595 | 514984.1488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -2987.6289 |  | -10514.9419 | -29573.2742 | -1683.3175 | 2510.5468 | -12873.5559 | -39260.9869 | -52134.5428
301 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.3297 | 2125 | 2125 | 22 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2365.2062 |  | 85810.1664 | 241341.093 | 12428.8862 | 111859.9757 | 50013.1844 | 451440.1214 | 501453.3058 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -2703.0928 |  | -10514.9419 | -29573.2742 | -1523.0016 | 2271.4471 | -12361.1398 | -39339.7706 | -51700.9104
302 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 5.9219 | 2175 | 2175 | 22 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 2628.0069 |  | 85810.1664 | 241341.093 | 13809.8735 | 124288.8619 | 50476.1058 | 465249.9949 | 515726.1008 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3003.4365 |  | -10514.9419 | -29573.2742 | -1692.2239 | 2523.8301 | -12890.8675 | -39256.61 | -52147.4775
303 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 7.8855 | 2400 | 2400 | 24 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 3499.3987 |  | 85810.1664 | 241341.093 | 18388.9369 | 165500.4319 | 51955.5695 | 511040.6283 | 562996.1978 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -3999.3128 |  | -10514.9419 | -29573.2742 | -2253.3298 | 3360.679 | -14583.9201 | -38980.8669 | -53564.787
304 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.5997 | 2575 | 2575 | 26 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 4260.1375 |  | 85810.1664 | 241341.093 | 22386.5319 | 201478.7867 | 53226.2474 | 551016.578 | 604242.8254 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -4868.7286 |  | -10514.9419 | -29573.2742 | -2743.1841 | 4091.2614 | -16038.0763 | -38740.1388 | -54778.2151
305 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 5 | 120 | 0 | 100 | ISO 5 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.4724 | 2675 | 2675 | 28 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 4647.4228 |  | 85810.1664 | 241341.093 | 24421.6711 | 219795.0401 | 53825.2179 | 571367.9706 | 625193.1886 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -5311.3403 |  | -10514.9419 | -29573.2742 | -2992.5645 | 4463.1943 | -16723.6083 | -38617.5863 | -55341.1947
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 165.7043 | 42375 | 42375 | 434 | 108.5 |  | 76.5 | 108.5
Zoning Area AHU - 19 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
306 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
307 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.0256 | 2850 | 2850 | 12 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 3 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5271.1949 | 2008.0742 | 627.5232 | 1647.2484 | 11634.84 | 6824 | 578.2316 | 17496 | 6224.2269 |  | 42905.0832 | 241341.093 | 32707.5952 | 294368.3572 | 48028.4934 | 611322.1287 | 659350.6222 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6024.2227 | -6024.2227 | 627.5232 | -1882.5696 | -13296.96 | 6824 | 578.2316 | 17496 | -7113.4022 |  | -5257.471 | -29573.2742 | -4007.8988 | 5977.4923 | -2791.3997 | -32861.1517 | -35652.5513
308 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.1712 | 2200 | 2200 | 10 | 5.5 | C | 4.5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 2738.6598 |  | 85810.1664 | 241341.093 | 14391.3419 | 129522.0772 | 50684.8917 | 471064.6785 | 521749.5702 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -3129.897 |  | -10514.9419 | -29573.2742 | -1763.4755 | 2630.0966 | -13129.7639 | -39221.595 | -52351.3589
309 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.5453 | 2250 | 2250 | 10 | 6 | C | 5 | 6 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 2904.6392 |  | 85810.1664 | 241341.093 | 15263.5444 | 137371.9 | 57953.8503 | 479786.7039 | 537740.5543 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -3319.5877 |  | -10514.9419 | -29573.2742 | -1870.3528 | 2789.4964 | -6814.7142 | -39169.0725 | -45983.7867
310 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.4542 | 2375 | 2375 | 10 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 5083.1186 |  | 0 | 241341.093 | 26711.2028 | 240400.8251 | 31383.123 | 508453.1209 | 539836.2439 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -5809.2785 |  | 0 | -29573.2742 | -3273.1174 | 4881.6187 | 8923.3816 | -27964.7728 | -19041.3912
311 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 16.8307 | 3375 | 3375 | 14 | 8.5 | C | 5 | 8.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 7469.0723 |  | 85810.1664 | 241341.093 | 39249.1143 | 353242.0287 | 58226.7979 | 719642.4024 | 777869.2003 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -8536.0826 |  | -10514.9419 | -29573.2742 | -4809.4786 | 7172.9908 | -21761.229 | -37724.7039 | -59485.933
312 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 24.872 | 4450 | 4450 | 18 | 11.5 | C | 7 | 11.5 |  | 5800 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 11037.6291 |  | 128715.2496 | 241341.093 | 58001.4689 | 522013.2201 | 81727.8063 | 950071.0317 | 1031798.838 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -12614.4332 |  | -15772.4129 | -29573.2742 | -7107.3406 | 10600.0864 | -34005.8283 | -41852.9413 | -75858.7696
313 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.5607 | 2900 | 2900 | 12 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 5574.141 |  | 85810.1664 | 241341.093 | 29291.4686 | 263623.2177 | 55277.2947 | 620065.9458 | 675343.2405 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -6370.4468 |  | -10514.9419 | -29573.2742 | -3589.2961 | 5353.1765 | -18385.5037 | -38324.3357 | -56709.8394
314 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.1063 | 2500 | 2500 | 10 | 6.5 | C | 6 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 3153.6083 |  | 128715.2496 | 241341.093 | 16571.8483 | 149146.6343 | 66448.7887 | 535774.8253 | 602223.6139 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -3604.1238 |  | -15772.4129 | -29573.2742 | -2030.6687 | 3028.5961 | -23835.2829 | -44347.7597 | -68183.0426
315 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 13.558 | 3000 | 3000 | 12 | 7.5 | C | 5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 6016.7527 |  | 85810.1664 | 241341.093 | 31617.3421 | 284556.0786 | 55936.7316 | 643324.6802 | 699261.4117 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -6876.2888 |  | -10514.9419 | -29573.2742 | -3874.3022 | 5778.2426 | -19140.2821 | -38184.2757 | -57324.5578
316 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.4803 | 2350 | 2350 | 10 | 6 | C | 4.5 | 6 |  | 5400 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3865.5429 | 1472.5878 | 334.679 | 878.5325 | 23269.68 | 3412 | 308.3902 | 17496 | 3319.5877 |  | 85810.1664 | 241341.093 | 17444.0508 | 156996.4572 | 51671.2008 | 501591.7674 | 553262.9683 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4417.7633 | -4417.7633 | 334.679 | -1004.0371 | -26593.92 | 3412 | 308.3902 | 17496 | -3793.8145 |  | -10514.9419 | -29573.2742 | -2137.546 | 3187.9959 | -14258.4657 | -39037.7663 | -53296.232
317 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 5.8907 | 2175 | 2175 | 10 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 263.5597 | 691.8443 | 23269.68 | 3412 | 242.8573 | 17496 | 2614.1753 |  | 85810.1664 | 241341.093 | 13737.19 | 123634.71 | 50460.9893 | 464523.1595 | 514984.1488 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 263.5597 | -790.6792 | -26593.92 | 3412 | 242.8573 | 17496 | -2987.6289 |  | -10514.9419 | -29573.2742 | -1683.3175 | 2510.5468 | -12873.5559 | -39260.9869 | -52134.5428
318 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.3297 | 2125 | 2125 | 10 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3250.5702 | 1238.3124 | 238.4588 | 625.9544 | 23269.68 | 3412 | 219.728 | 17496 | 2365.2062 |  | 85810.1664 | 241341.093 | 12428.8862 | 111859.9757 | 50013.1844 | 451440.1214 | 501453.3058 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3714.9373 | -3714.9373 | 238.4588 | -715.3764 | -26593.92 | 3412 | 219.728 | 17496 | -2703.0928 |  | -10514.9419 | -29573.2742 | -1523.0016 | 2271.4471 | -12361.1398 | -39339.7706 | -51700.9104
319 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 5.9219 | 2175 | 2175 | 10 | 5.5 | C | 4.5 | 5.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3426.2767 | 1305.2483 | 264.9542 | 695.5049 | 23269.68 | 3412 | 244.1422 | 17496 | 2628.0069 |  | 85810.1664 | 241341.093 | 13809.8735 | 124288.8619 | 50476.1058 | 465249.9949 | 515726.1008 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -3915.7448 | -3915.7448 | 264.9542 | -794.8627 | -26593.92 | 3412 | 244.1422 | 17496 | -3003.4365 |  | -10514.9419 | -29573.2742 | -1692.2239 | 2523.8301 | -12890.8675 | -39256.61 | -52147.4775
320 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 7.8855 | 2400 | 2400 | 10 | 6 | C | 4.5 | 6 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3953.3962 | 1506.0557 | 352.8075 | 926.1197 | 23269.68 | 3412 | 325.0947 | 17496 | 3499.3987 |  | 85810.1664 | 241341.093 | 18388.9369 | 165500.4319 | 51955.5695 | 511040.6283 | 562996.1978 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4518.167 | -4518.167 | 352.8075 | -1058.4225 | -26593.92 | 3412 | 325.0947 | 17496 | -3999.3128 |  | -10514.9419 | -29573.2742 | -2253.3298 | 3360.679 | -14583.9201 | -38980.8669 | -53564.787
321 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.5997 | 2575 | 2575 | 12 | 6.5 | C | 4.5 | 6.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4392.6624 | 1673.3952 | 429.5048 | 1127.45 | 23269.68 | 3412 | 395.7674 | 17496 | 4260.1375 |  | 85810.1664 | 241341.093 | 22386.5319 | 201478.7867 | 53226.2474 | 551016.578 | 604242.8254 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5020.1856 | -5020.1856 | 429.5048 | -1288.5143 | -26593.92 | 3412 | 395.7674 | 17496 | -4868.7286 |  | -10514.9419 | -29573.2742 | -2743.1841 | 4091.2614 | -16038.0763 | -38740.1388 | -54778.2151
322 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 24 | 50 | 45 | 85 | ISO 7 | 120 | 0 | 100 | ISO 7 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.4724 | 2675 | 2675 | 12 | 7 | C | 4.5 | 7 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4568.3689 | 1740.331 | 468.5507 | 1229.9455 | 23269.68 | 3412 | 431.7463 | 17496 | 4647.4228 |  | 85810.1664 | 241341.093 | 24421.6711 | 219795.0401 | 53825.2179 | 571367.9706 | 625193.1886 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5220.993 | -5220.993 | 468.5507 | -1405.652 | -26593.92 | 3412 | 431.7463 | 17496 | -5311.3403 |  | -10514.9419 | -29573.2742 | -2992.5645 | 4463.1943 | -16723.6083 | -38617.5863 | -55341.1947
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 165.7043 | 42375 | 42375 | 182 | 108.5 |  | 76.5 | 108.5
Zoning Area AHU - 20 Air-Conditioning System (Chilled Water) | [41 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
323 | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Chilled Water (C) OR DX (D) | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
324 | Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 96.84 | 762.3245 | 1524.649 | 152.4649 | 0 | 14.5132 | 2850 | 2850 | 12 | 7.5 | C | 4.5 | 7.5 | 42500 | W | 150 | 1120 | 60 | 4 | 108.5 | 4 | 434 | 27.3811 | 2 | 132.0612 |  |  |  |  | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 6024.2227 | 2008.0742 | 627.5232 | 1882.5696 | 13296.96 | 6824 | 578.2316 | 17496 | 7113.4022 |  | 44396.8871 | 249732.4899 | 33844.8339 | 304603.5048 | 51332.8165 | 632577.7157 | 683910.5323 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -5271.1949 | -5271.1949 | 627.5232 | -1647.2484 | -11634.84 | 6824 | 578.2316 | 17496 | -6224.2269 |  | -3765.6671 | -21181.8773 | -2870.6602 | 4299.4782 | 748.2446 | -23518.7264 | -22770.4818
325 | Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 42.6096 | 335.4228 | 670.8455 | 67.0846 | 0 | 6.3858 | 2200 | 2200 | 10 | 5.5 | C | 5 | 5.5 |  | 4000 | [14 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 4016.1485 | 1338.7162 | 276.1102 | 828.3306 | 26593.92 | 3412 | 254.4219 | 17496 | 3129.897 |  | 88793.7742 | 249732.4899 | 14891.7269 | 134025.5421 | 54902.3874 | 487443.5331 | 542345.9205 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -3514.1299 | -3514.1299 | 276.1102 | -724.7893 | -23269.68 | 3412 | 254.4219 | 17496 | -2738.6598 |  | -7531.3342 | -21181.8773 | -1263.0905 | 1891.7704 | -8808.7269 | -28084.5316 | -36893.2585
326 | Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 45.192 | 355.7514 | 711.5028 | 71.1503 | 0 | 6.7728 | 2250 | 2250 | 10 | 6 | C | 5.5 | 6 |  | H | [14 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 4317.3596 | 1439.1199 | 292.8442 | 878.5325 | 26593.92 | 10236 | 269.8414 | 17496 | 3319.5877 |  | 88793.7742 | 249732.4899 | 15794.2558 | 142148.3023 | 62232.7087 | 496468.8222 | 558701.5309 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -3777.6897 | -3777.6897 | 292.8442 | -768.7159 | -23269.68 | 10236 | 269.8414 | 17496 | -2904.6392 |  | -7531.3342 | -21181.8773 | -1339.6414 | 2006.4232 | -2426.0392 | -28046.4298 | -30472.469
327 | Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 79.086 | 622.565 | 1245.13 | 124.513 | 0 | 11.8525 | 2375 | 2375 | 10 | 6 | C | 3 | 6 |  | 3600 | [14 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 5622.6079 | 1874.2026 | 512.4773 | 1537.4318 | 0 | 3412 | 472.2225 | 17496 | 5809.2785 |  | 0 | 249732.4899 | 27639.9477 | 248759.5289 | 32812.1088 | 526131.9665 | 558944.0753 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -4919.7819 | -4919.7819 | 512.4773 | -1345.2529 | 0 | 3412 | 472.2225 | 17496 | -5083.1186 |  | 0 | -21181.8773 | -2344.3725 | 3511.2405 | 10544.5464 | -20015.0093 | -9470.4629
328 | Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 116.208 | 914.7894 | 1829.5788 | 182.9579 | 0 | 17.4159 | 3375 | 3375 | 14 | 8.5 | C | 5.5 | 8.5 |  | L | [14 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 6727.0487 | 2242.3496 | 753.0278 | 2259.0835 | 26593.92 | 3412 | 693.878 | 17496 | 8536.0826 |  | 88793.7742 | 249732.4899 | 40613.8006 | 365524.2058 | 63458.9293 | 744664.2705 | 808123.1998 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -5886.1676 | -5886.1676 | 753.0278 | -1976.6981 | -23269.68 | 3412 | 693.878 | 17496 | -7469.0723 |  | -7531.3342 | -21181.8773 | -3444.7922 | 5159.3738 | -16246.7122 | -26998.6299 | -43245.3421
329 | Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 171.7296 | 1351.8554 | 2703.7108 | 270.3711 | 0 | 25.7368 | 4450 | 4450 | 18 | 11.5 | C | 7.5 | 11.5 |  | 6800 | [14 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 8032.297 | 2677.4323 | 1112.8078 | 3338.4234 | 39890.88 | 10236 | 1025.3974 | 17496 | 12614.4332 |  | 133190.6613 | 249732.4899 | 60018.1721 | 540163.5486 | 89295.0076 | 983104.8718 | 1072399.8794 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -7028.2598 | -7028.2598 | 1112.8078 | -2921.1205 | -34904.52 | 10236 | 1025.3974 | 17496 | -11037.6291 |  | -11297.0012 | -21181.8773 | -5090.6374 | 7624.408 | -26021.3241 | -29945.108 | -55966.4322
330 | Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 86.7256 | 682.7039 | 1365.4078 | 136.5408 | 0 | 12.9974 | 2900 | 2900 | 12 | 7.5 | C | 5.5 | 7.5 | [16 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 5723.0116 | 1907.6705 | 561.9819 | 1685.9457 | 26593.92 | 3412 | 517.8386 | 17496 | 6370.4468 |  | 88793.7742 | 249732.4899 | 30309.929 | 272789.361 | 60113.217 | 641625.5541 | 701738.7711 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -5007.6351 | -5007.6351 | 561.9819 | -1475.2025 | -23269.68 | 3412 | 517.8386 | 17496 | -5574.141 |  | -7531.3342 | -21181.8773 | -2570.8357 | 3850.4216 | -13338.8381 | -27433.6256 | -40772.4637
331 | Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 49.0656 | 386.2444 | 772.4888 | 77.2489 | 0 | 7.3534 | 2500 | 2500 | 10 | 6.5 | C | 6.5 | 6.5 | [16 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 4317.3596 | 1439.1199 | 317.9451 | 953.8353 | 39890.88 | 6824 | 292.9707 | 17496 | 3604.1238 |  | 133190.6613 | 249732.4899 | 17148.0492 | 154332.4424 | 72425.3341 | 554403.6428 | 626828.9769 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -3777.6897 | -3777.6897 | 317.9451 | -834.6059 | -34904.52 | 6824 | 292.9707 | 17496 | -3153.6083 |  | -11297.0012 | -21181.8773 | -1454.4678 | 2178.4023 | -17739.508 | -31754.9441 | -49494.4522
332 | Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 93.612 | 736.9137 | 1473.8273 | 147.3827 | 0 | 14.0295 | 3000 | 3000 | 12 | 7.5 | C | 5.5 | 7.5 | [16 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 5923.819 | 1974.6063 | 606.6058 | 1819.8173 | 26593.92 | 3412 | 558.9573 | 17496 | 6876.2888 |  | 88793.7742 | 249732.4899 | 32716.6727 | 294450.0547 | 60860.985 | 665692.9915 | 726553.9766 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -5183.3416 | -5183.3416 | 606.6058 | -1592.3401 | -23269.68 | 3412 | 558.9573 | 17496 | -6016.7527 |  | -7531.3342 | -21181.8773 | -2774.9715 | 4156.1622 | -13988.5514 | -27332.0208 | -41320.5722
333 | Clean Room 19 | 2.4 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 51.648 | 406.5731 | 813.1461 | 81.3146 | 0 | 7.7404 | 2350 | 2350 | 10 | 6 | C | 5 | 6 |  | 6400 | [14 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 4417.7633 | 1472.5878 | 334.679 | 1004.0371 | 26593.92 | 3412 | 308.3902 | 17496 | 3793.8145 |  | 88793.7742 | 249732.4899 | 18050.5781 | 162455.2026 | 56021.888 | 519032.0447 | 575053.9328 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -3865.5429 | -3865.5429 | 334.679 | -878.5325 | -23269.68 | 3412 | 308.3902 | 17496 | -3319.5877 |  | -7531.3342 | -21181.8773 | -1531.0188 | 2293.055 | -9782.2738 | -27951.1752 | -37733.4491
334 | Clean Room 20 | 2.1 | 1.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 40.6728 | 320.1763 | 640.3526 | 64.0353 | 0 | 6.0956 | 2175 | 2175 | 10 | 5.5 | C | 5 | 5.5 | [16 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 3915.7448 | 1305.2483 | 263.5597 | 790.6792 | 26593.92 | 3412 | 242.8573 | 17496 | 2987.6289 |  | 88793.7742 | 249732.4899 | 14214.8302 | 127933.472 | 54648.151 | 480674.5664 | 535322.7173 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -3426.2767 | -3426.2767 | 263.5597 | -691.8443 | -23269.68 | 3412 | 242.8573 | 17496 | -2614.1753 |  | -7531.3342 | -21181.8773 | -1205.6773 | 1805.7808 | -8587.5593 | -28113.1079 | -36700.6672
335 | Clean Room 21 | 1.8 | 1.9 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 36.7992 | 289.6833 | 579.3666 | 57.9367 | 0 | 5.515 | 2125 | 2125 | 10 | 5.5 | C | 5 | 5.5 | [16 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 3714.9373 | 1238.3124 | 238.4588 | 715.3764 | 26593.92 | 3412 | 219.728 | 17496 | 2703.0928 |  | 88793.7742 | 249732.4899 | 12861.0369 | 115749.3318 | 54139.6782 | 467136.6328 | 521276.311 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -3250.5702 | -3250.5702 | 238.4588 | -625.9544 | -23269.68 | 3412 | 219.728 | 17496 | -2365.2062 |  | -7531.3342 | -21181.8773 | -1090.8509 | 1633.8017 | -8145.224 | -28170.2607 | -36315.4846
336 | Clean Room 22 | 1.9 | 2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 40.888 | 321.8703 | 643.7407 | 64.3741 | 0 | 6.1278 | 2175 | 2175 | 10 | 5.5 | C | 5 | 5.5 | [16 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 3915.7448 | 1305.2483 | 264.9542 | 794.8627 | 26593.92 | 3412 | 244.1422 | 17496 | 3003.4365 |  | 88793.7742 | 249732.4899 | 14290.041 | 128610.3687 | 54665.2435 | 481426.6738 | 536091.9173 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -3426.2767 | -3426.2767 | 264.9542 | -695.5049 | -23269.68 | 3412 | 244.1422 | 17496 | -2628.0069 |  | -7531.3342 | -21181.8773 | -1212.0565 | 1815.3352 | -8602.372 | -28109.9328 | -36712.3048
337 | Clean Room 23 | 2.3 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 54.4456 | 428.5958 | 857.1915 | 85.7192 | 0 | 8.1597 | 2400 | 2400 | 10 | 6 | C | 5 | 6 | [16 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 4518.167 | 1506.0557 | 352.8075 | 1058.4225 | 26593.92 | 3412 | 325.0947 | 17496 | 3999.3128 |  | 88793.7742 | 249732.4899 | 19028.3177 | 171254.8594 | 56344.4945 | 528809.4412 | 585153.9357 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -3953.3962 | -3953.3962 | 352.8075 | -926.1197 | -23269.68 | 3412 | 325.0947 | 17496 | -3499.3987 |  | -7531.3342 | -21181.8773 | -1613.949 | 2417.2622 | -10062.6923 | -27909.8983 | -37972.5906
338 | Clean Room 24 | 2.2 | 2.8 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 66.2816 | 521.7688 | 1043.5375 | 104.3538 | 0 | 9.9335 | 2575 | 2575 | 12 | 6.5 | C | 5 | 6.5 | [16 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 5020.1856 | 1673.3952 | 429.5048 | 1288.5143 | 26593.92 | 3412 | 395.7674 | 17496 | 4868.7286 |  | 88793.7742 | 249732.4899 | 23164.9085 | 208484.1766 | 57786.6016 | 570175.3493 | 627961.9509 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -4392.6624 | -4392.6624 | 429.5048 | -1127.45 | -23269.68 | 3412 | 395.7674 | 17496 | -4260.1375 |  | -7531.3342 | -21181.8773 | -1964.8074 | 2942.754 | -11316.6577 | -27735.265 | -39051.9227
339 | Clean Room 25 | 2.8 | 2.4 | 2.4 | 2 | 1 | 1.75 | 3 | 10% | 0% | 21 | 50 | 45 | 85 | ISO 8 | 120 | 0 | 100 | ISO 8 | 120 | 72.3072 | 569.2023 | 1138.4046 | 113.8405 | 0 | 10.8365 | 2675 | 2675 | 12 | 7 | C | 5 | 7 | [16 empty] | 14.4 | 43.2 | 29 | 85 | 151.3793 | 21 | 50 | 54.0935 | 97.2858 | 45 | 85 | 380.5412 | 21 | 50 | 54.0935 | 326.4477 | 5220.993 | 1740.331 | 468.5507 | 1405.652 | 26593.92 | 3412 | 431.7463 | 17496 | 5311.3403 |  | 88793.7742 | 249732.4899 | 25270.8093 | 227437.2836 | 58465.9996 | 591234.357 | 649700.3566 | 14.4 | -37.8 | 13 | 90 | 58.7013 | 21 | 50 | 54.0935 | 4.6078 | 0 | 100 | 26.4048 | 21 | 50 | 54.0935 | -27.6887 | -4568.3689 | -4568.3689 | 468.5507 | -1229.9455 | -23269.68 | 3412 | 431.7463 | 17496 | -4647.4228 |  | -7531.3342 | -21181.8773 | -2143.4263 | 3210.277 | -11907.1202 | -27646.3607 | -39553.4809
[21 empty] | 1144.1108 | 9006.4402 | 18012.8804 | 1801.288 | 0 | 171.4658 | 42375 | 42375 | 182 | 108.5 |  | 83.5 | 108.5

## BOD-Hot & Cold
VLOOKUP(A30,$C$35:$F$254,4,FALSE)
Zoning Area 1(AHU - No.: ) Chilled water System / Cooling System | [40 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
S.No. | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No.of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/- 5% | Peak Max Temp.(Out) in ˚C | RH(Out) in +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area | Volume | Room Cfm | FA | EA | Rem. Water vapour Kg/hr | Deh. Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Cooling Load in TR | Room AC load in TR | Cfm AC load in TR | AHU Cfm | AHU Size | Static Pressure | Blower Model BDB | Motor Selected in Hp | No. of Rows of Cooling Coil | AHU Cooling Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size in mm | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity | Pipe Size | Delta T(AHU) | Delta T Out | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in C | RH in % | W Return | Temp in C | RH in % | W in | Delta W AHU | Temp in C | RH in % | W out | Temp in C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
| Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 15% | 5% | 24 | 50 | 43.1 | 100 | ISO 6 | 180 | -16.6 | 8 | ISO 6 | 180 | 96.84 | 762.3245 | 2286.9734 | 343.046 | 114.3487 | 34.3161 | 3750 | 3750 | 38 | 9.5 | 5 | 9.5 | 33250 | W | 150 | #NAME? | 50 | 4 | 84.5 | 4 | 338 | 21.3244 | 2 | 116.5437 |  |  |  |  | 14.4 | 34.38 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 43.1 | 100 | 408.118 | 24 | 50 | 65.0626 | 343.0554 | 4794.2772 | 2008.0742 | 627.5232 | 1498.2116 | 10582.164 | 6824 | 578.2316 | 17496 | 16983.2477 |  | 46655.5281 | 262437.3458 | 106699.9537 | 453474.8032 | 57257.9206 | 869267.6309 | 926525.5515 | 14.4 | -73.08 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | -16.6 | 8 | 0.57291 | 24 | 50 | 65.0626 | -64.4897 | -10190.9768 | -10190.9768 | 627.5232 | -3184.6802 | -22494.024 | 6824 | 578.2316 | 17496 | -36100.5161 |  | -8770.6038 | -49334.6462 | -20058.1379 | 8468.1142 | -46444.4423 | -69695.2737 | -116139.716
| Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 42.6096 | 335.4228 | 1006.2683 | 150.9402 | 50.3134 | 13.8853 | 2600 | 2600 | 26 | 6.5 | 5 | 6.5 |  | 3600 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | 1338.7162 | 276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | 17496 | 8215.9795 |  | 85810.1664 | 241341.093 | 43174.0257 | 183489.6093 | 56162.2114 | 553814.8945 | 609977.1059 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -9389.6909 |  | -10514.9419 | -29573.2742 | -5290.4264 | 3725.9702 | -19389.5579 | -41652.6724 | -61042.2302
| Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 45.192 | 355.7514 | 1067.2543 | 160.0881 | 53.3627 | 14.7268 | 2650 | 2650 | 28 | 7 | 5.5 | 7 |  | H | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | 17496 | 8713.9177 |  | 85810.1664 | 241341.093 | 45790.6333 | 194610.1917 | 63763.1288 | 567552.0845 | 631315.2133 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -9958.7631 |  | -10514.9419 | -29573.2742 | -5611.0584 | 3951.7866 | -13453.8896 | -41747.4879 | -55201.3775
| Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 79.086 | 622.565 | 1867.695 | 280.1542 | 93.3847 | 25.772 | 3100 | 3100 | 32 | 8 | 3.5 | 8 |  | 2900 | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | 1874.2026 | 512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | 17496 | 15249.3559 |  | 0 | 241341.093 | 80133.6084 | 340567.8355 | 41549.3603 | 662042.5369 | 703591.8972 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -17427.8354 |  | 0 | -29573.2742 | -9819.3521 | 6915.6266 | -2695.1753 | -32476.9998 | -35172.175
| Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 116.208 | 914.7894 | 2744.3681 | 411.6552 | 137.2184 | 37.869 | 4425 | 4425 | 46 | 11.5 | 6.5 | 11.5 |  | L | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | 2242.3496 | 753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | 17496 | 22407.2169 |  | 85810.1664 | 241341.093 | 117747.3429 | 500426.2073 | 73164.9425 | 945324.8096 | 1018489.7521 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -25608.2479 |  | -10514.9419 | -29573.2742 | -14428.4358 | 10161.737 | -38833.3943 | -44354.9149 | -83188.3092
| Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 171.7296 | 1351.8554 | 4055.5662 | 608.3349 | 202.7783 | 55.962 | 6000 | 6000 | 60 | 15 | 9 | 15 |  | #NAME? | [14 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | 2677.4323 | 1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | 17496 | 33112.8872 |  | 128715.2496 | 241341.093 | 174004.4067 | 739518.7285 | 103803.0645 | 1283579.4779 | 1387382.5424 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -37843.2996 |  | -15772.4129 | -29573.2742 | -21322.0217 | 15016.7891 | -59234.6948 | -51650.9198 | -110885.6145
| Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 86.7256 | 682.7039 | 2048.1118 | 307.2168 | 102.4056 | 28.2615 | 3700 | 3700 | 38 | 9.5 | 6 | 9.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | 1907.6705 | 561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | 17496 | 16722.423 |  | 85810.1664 | 241341.093 | 87874.4059 | 373466.2251 | 66425.5767 | 788491.8904 | 854917.4671 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -19111.3405 |  | -10514.9419 | -29573.2742 | -10767.8882 | 7583.6667 | -31126.3973 | -43272.4376 | -74398.835
| Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 49.0656 | 386.2444 | 1158.7332 | 173.81 | 57.9367 | 15.9891 | 2950 | 2950 | 30 | 7.5 | 6.5 | 7.5 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | 1439.1199 | 317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | 17496 | 9460.8249 |  | 128715.2496 | 241341.093 | 49715.5448 | 211291.0653 | 72756.0053 | 631062.9527 | 703818.958 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -10812.3713 |  | -15772.4129 | -29573.2742 | -6092.0062 | 4290.5112 | -31043.5304 | -47147.1822 | -78190.7126
| Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 93.612 | 736.9137 | 2210.741 | 331.6111 | 110.537 | 30.5056 | 3850 | 3850 | 40 | 10 | 6 | 10 | [16 empty] | 14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | 1974.6063 | 606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | 17496 | 18050.2581 |  | 85810.1664 | 241341.093 | 94852.0262 | 403121.1114 | 67970.2369 | 825124.3971 | 893094.634 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -20628.8663 |  | -10514.9419 | -29573.2742 | -11622.9066 | 8185.8437 | -32892.8596 | -43525.279 | -76418.1387
[21 empty] | 781.0684 | 6148.5704 | 18445.7113 | 2766.8567 | 922.2856 | 257.2875 | 33025 | 33025 | 338 | 84.5 | 53 | 84.5
Zoning Area 1 ( AHU No.: ) Hot water System / Heating System | [40 empty] | Chilled Water Details |  |  |  | Hot Water/Steam Details |  |  |  | Cooling Load Calculations | [15 empty] | Sensible Heat Load for Cooling / AC | [9 empty] | Latent Heat Load for Cooling / AC |  |  |  | Total Enthalpy for Cooling / AC |  |  | Heating Load Calculations | [15 empty] | Sensible Heat Load for Heating | [9 empty] | Latent Heat Load for Heating
S.No. | Room Name | Length in mtrs | Width in mtrs | Height in mtrs | People in Nos | Eqpt. Load in KW | Lighting in W/Sft | No. of Inf./Hr | Fresh Air | Exhaust | T ˚C (Required inside) | RH(in) +/-5% | Peak Max Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Peak Min Temp.(Out) in ˚C | RH(Out) +/- 5% | Class | ACPH | Area in Sft | Volume in Cu. Ft | Room Cfm | Fresh Air Cfm | Exhaust Air iCfm | Add Water vapour in Kg/hr | Humidification Cfm | Res. Cfm | Room Terminal Supply Module in Sft | Res. Heating Load in TR | Room Heating load in TR | Cfm Heating load in TR | AHU Cfm | AHU Size | Static Pressure in mm of WC | Blower Selected | Motor Selected in Hp | No. of Rows of Heating Coil | AHU Heating Load in TR | No. Of Stages of Filtr. | Chilled water in GPM | Chilled water in L/s | Flow Velocity in m/s | Pipe Size | Hot Water/Steam in GPM | Hot water/Steam in L/s | Flow Velocity in m/s | Pipe Size | Delta T(AHU) in ˚F | Delta T Out in ˚F | Temp inin ˚ C | RH in % | W Return | Temp in in ˚C | RH in % | W in | Delta W AHU | Temp in in ˚C | RH in % | W out | Temp in in ˚C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH | Delta T(AHU) Peak Min ˚F | Delta T Out Peak Min ˚F | Temp in in ˚C | RH in % | W Return | Temp in in ˚C | RH in % | W in | Delta W AHU | Temp in in ˚C | RH in % | W out | Temp in in ˚C | RH in % | W in | Delta W Out | Wall | Partition | Roof | Floor | People | Eqpt. Load | Lighting | Inf./Hr 375 Cfm door 3'x7'-30sec | Fresh Air | Exhaust | People | Inf./Hr | Fresh Air | Return Air | ERSH | ERLH | ERTH
| Clean Room 10 | 3 | 3 | 2.4 | 1 | 2 | 1.75 | 3 | 15% | 5% | 24 | 50 | 43.1 | 100 | ISO 6 | 180 | -16.6 | 8 | ISO 6 | 180 | 96.84 | 762.3245 | 2286.9734 | 343.046 | 114.3487 | 6.451 | 1600 | 2650 | 28 | 10 | 10 | 7 |  | W | 150 | Refer | #VALUE! | 4 | 66 | 4 |  |  |  |  | 240 | 15.1416 | 1.4201 | 116.5437 | -14.4 | 34.38 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 43.1 | 100 | 408.118 | 24 | 50 | 65.0626 | 343.0554 | 4794.2772 | -2008.0742 | -627.5232 | 1498.2116 | 10582.164 | 6824 | 578.2316 | -17496 | 16983.2477 |  | 46655.5281 | 262437.3458 | 106699.9537 | 453474.8032 | 22265.9206 | 869267.6309 | 891533.5515 | 14.4 | -73.08 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | -16.6 | 8 | 0.57291 | 24 | 50 | 65.0626 | -64.4897 | -10190.9768 | -10190.9768 | 627.5232 | -3184.6802 | -22494.024 | 6824 | 578.2316 | 17496 | -36100.5161 |  | -8770.6038 | -49334.6462 | -20058.1379 | 8468.1142 | -46444.4423 | -69695.2737 | -116139.716
| Clean Room 11 | 1.8 | 2.2 | 2.4 | 2 | 1 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 42.6096 | 335.4228 | 1006.2683 | 150.9402 | 50.3134 | 1.7015 | 1600 | 1600 | 16 | 5.5 | 5.5 | 4 |  | 3600 | [14 empty] | -14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3514.1299 | -1338.7162 | -276.1102 | 724.7893 | 23269.68 | 3412 | 254.4219 | -17496 | 8215.9795 |  | 85810.1664 | 241341.093 | 43174.0257 | 183489.6093 | 21170.2114 | 553814.8945 | 574985.1059 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4016.1485 | -4016.1485 | 276.1102 | -828.3306 | -26593.92 | 3412 | 254.4219 | 17496 | -9389.6909 |  | -10514.9419 | -29573.2742 | -5290.4264 | 3725.9702 | -19389.5579 | -41652.6724 | -61042.2302
| Clean Room 12 | 1.5 | 2.8 | 2.4 | 2 | 3 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 45.192 | 355.7514 | 1067.2543 | 160.0881 | 53.3627 | 1.8046 | 1600 | 1600 | 16 | 5 | 5 | 4 |  | H | [14 empty] | -14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | -1439.1199 | -292.8442 | 768.7159 | 23269.68 | 10236 | 269.8414 | -17496 | 8713.9177 |  | 85810.1664 | 241341.093 | 45790.6333 | 194610.1917 | 28771.1288 | 567552.0845 | 596323.2133 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 292.8442 | -878.5325 | -26593.92 | 10236 | 269.8414 | 17496 | -9958.7631 |  | -10514.9419 | -29573.2742 | -5611.0584 | 3951.7866 | -13453.8896 | -41747.4879 | -55201.3775
| Clean Room 13 | 2.1 | 3.5 | 2.4 | 0 | 1 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 79.086 | 622.565 | 1867.695 | 280.1542 | 93.3847 | 3.158 | 1250 | 2150 | 22 | 5.5 | 3 | 5.5 |  | 2900 | [14 empty] | -14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 4919.7819 | -1874.2026 | -512.4773 | 1345.2529 | 0 | 3412 | 472.2225 | -17496 | 15249.3559 |  | 0 | 241341.093 | 80133.6084 | 340567.8355 | 6557.3603 | 662042.5369 | 668599.8972 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5622.6079 | -5622.6079 | 512.4773 | -1537.4318 | 0 | 3412 | 472.2225 | 17496 | -17427.8354 |  | 0 | -29573.2742 | -9819.3521 | 6915.6266 | -2695.1753 | -32476.9998 | -35172.175
| Clean Room 14 | 2.7 | 4 | 2.4 | 2 | 1 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 116.208 | 914.7894 | 2744.3681 | 411.6552 | 137.2184 | 4.6404 | 1700 | 3175 | 32 | 8 | 7 | 8 |  | L | [14 empty] | -14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5886.1676 | -2242.3496 | -753.0278 | 1976.6981 | 23269.68 | 3412 | 693.878 | -17496 | 22407.2169 |  | 85810.1664 | 241341.093 | 117747.3429 | 500426.2073 | 38172.9425 | 945324.8096 | 983497.7521 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -6727.0487 | -6727.0487 | 753.0278 | -2259.0835 | -26593.92 | 3412 | 693.878 | 17496 | -25608.2479 |  | -10514.9419 | -29573.2742 | -14428.4358 | 10161.737 | -38833.3943 | -44354.9149 | -83188.3092
| Clean Room 15 | 3.8 | 4.2 | 2.4 | 3 | 3 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 171.7296 | 1351.8554 | 4055.5662 | 608.3349 | 202.7783 | 6.8574 | 1975 | 4675 | 48 | 12 | 9.5 | 12 |  | #NAME? | [14 empty] | -14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 7028.2598 | -2677.4323 | -1112.8078 | 2921.1205 | 34904.52 | 10236 | 1025.3974 | -17496 | 33112.8872 |  | 128715.2496 | 241341.093 | 174004.4067 | 739518.7285 | 68811.0645 | 1283579.4779 | 1352390.5424 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -8032.297 | -8032.297 | 1112.8078 | -3338.4234 | -39890.88 | 10236 | 1025.3974 | 17496 | -37843.2996 |  | -15772.4129 | -29573.2742 | -21322.0217 | 15016.7891 | -59234.6948 | -51650.9198 | -110885.6145
| Clean Room 16 | 3.1 | 2.6 | 2.4 | 2 | 1 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 86.7256 | 682.7039 | 2048.1118 | 307.2168 | 102.4056 | 3.4631 | 1650 | 2375 | 24 | 6.5 | 6.5 | 6 | [16 empty] | -14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5007.6351 | -1907.6705 | -561.9819 | 1475.2025 | 23269.68 | 3412 | 517.8386 | -17496 | 16722.423 |  | 85810.1664 | 241341.093 | 87874.4059 | 373466.2251 | 31433.5767 | 788491.8904 | 819925.4671 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5723.0116 | -5723.0116 | 561.9819 | -1685.9457 | -26593.92 | 3412 | 517.8386 | 17496 | -19111.3405 |  | -10514.9419 | -29573.2742 | -10767.8882 | 7583.6667 | -31126.3973 | -43272.4376 | -74398.835
| Clean Room 17 | 1.9 | 2.4 | 2.4 | 3 | 2 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 49.0656 | 386.2444 | 1158.7332 | 173.81 | 57.9367 | 1.9593 | 1800 | 1800 | 18 | 7 | 7 | 4.5 | [16 empty] | -14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 3777.6897 | -1439.1199 | -317.9451 | 834.6059 | 34904.52 | 6824 | 292.9707 | -17496 | 9460.8249 |  | 128715.2496 | 241341.093 | 49715.5448 | 211291.0653 | 37764.0053 | 631062.9527 | 668826.958 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -4317.3596 | -4317.3596 | 317.9451 | -953.8353 | -39890.88 | 6824 | 292.9707 | 17496 | -10812.3713 |  | -15772.4129 | -29573.2742 | -6092.0062 | 4290.5112 | -31043.5304 | -47147.1822 | -78190.7126
| Clean Room 18 | 3 | 2.9 | 2.4 | 2 | 1 | 1.75 | 3 | 15% | 5% | 24 | 50 | 45 | 85 | ISO 6 | 180 | 0 | 100 | ISO 6 | 180 | 93.612 | 736.9137 | 2210.741 | 331.6111 | 110.537 | 3.7381 | 1675 | 2550 | 26 | 6.5 | 6.5 | 6.5 | [16 empty] | -14.4 | 37.8 | 32 | 85 | 180.8634 | 24 | 50 | 65.0626 | 115.8008 | 45 | 85 | 380.5412 | 24 | 50 | 65.0626 | 315.4786 | 5183.3416 | -1974.6063 | -606.6058 | 1592.3401 | 23269.68 | 3412 | 558.9573 | -17496 | 18050.2581 |  | 85810.1664 | 241341.093 | 94852.0262 | 403121.1114 | 32978.2369 | 825124.3971 | 858102.634 | 14.4 | -43.2 | 16 | 90 | 71.4688 | 24 | 50 | 65.0626 | 6.4062 | 0 | 100 | 26.4048 | 24 | 50 | 65.0626 | -38.6579 | -5923.819 | -5923.819 | 606.6058 | -1819.8173 | -26593.92 | 3412 | 558.9573 | 17496 | -20628.8663 |  | -10514.9419 | -29573.2742 | -11622.9066 | 8185.8437 | -32892.8596 | -43525.279 | -76418.1387
[21 empty] | 781.0684 | 6148.5704 | 18445.7113 | 2766.8567 | 922.2856 | 33.7733 | 14850 | 22575 | 230 | 66 | 60 | 57.5 | [14 empty] | Flow velocity for Different Hot and Cold Condition piping

## BOQ
Sub.: Offer for Class 100K AC & Ventilation System and NC System for your PB - C and Pilot Plan Reg.
S.No. | Description & Specifications | [5 empty] | Units | Qty | Supply |  | Installation
[9 empty] | Rate | Amount | Rate | Amount
I | AIR HANDLING UNITS
| Supply, Installation, Testing & Commissioning of Factory assembled/ modular Single / Double Skin floor mounted type Air Handling Units (AHUs)(Single / Double Decker as per Plant Room Specs. AHUs shall be complete with Single skin 25 mm panels with 1.2mm Zinc / G.I. Sheets or double skin 25/47 mm thick insulated panels with CFC free polyurethane foam (PUF) insulation material with minimum density of 42 Kg/m3, sandwiched between 0.63/0.8 mm thick Aluminium Zinc / G.I.Sheets (inner skin) and pre-coated G.I. Sheets (outer skin). The AHUs shall be complete with mixing box with necessary openings and provosion for aluminium dampers for teminating return air and fresh air ducts. Food grade self-adhesive coated EPDM gaskets shall be provided between panels and structure of the AHU to ensure the entire housing is airtight, and should meet clean room class leakage requirments as per Standards. The AHUs shall be complete with provision for Fresh air filter section/ pre-filter section/ fine-filter or filters section/Superfine filter sections as mentioned below along without/with cooling coil section with specified multirows deep chilled water cooling coil of copper tube & aluminium fin construction to be sized for Cooling load specified with all controls & accessories, Re-heat section complete with finned type strip heaters, SS drain pan constructed from 18 gauge stainless steel & factory insulated with closed cell elastomeric Class 'O' material, copper header with "Copper to MS" adopter for Evaporator coil made out of 1/2" / 5/8" copper tubes with MS Header/Distributor with 12-13 FPI of mentioned capacities., all adaptive controls such as airstat, geyserstat, safetystat complete with wiring & vibration isolation pads etc. and all complete as per the specifications for Air-conditioning. AHUs shall be selected for a maximum face velocity of 500 FPM (2.5 MPS) and as per the Schedule of Air Handling Units. fan section with backward curved centrifugal fan (Kruger / Nicotra / Equivalent Make) with V-Belt drive arrangement and access doors where ever necessary with Motor (Crompton / equivalent Make) and Fan outlet velocity shall not exceed as per selected blower ratings and not more than 2000 FPM (10.2 MPS). AHUs should have marine lamps including adequately rated LED inside the AHU Cabinets. AHU inspection doors should have view windows with perfectly sealed gaksets on either side to ensure air tightness. All AHU doors shall be provided with door limit switch and door safety GI guard as well. | [34 empty] | Gear Type Aluminium Volume Control Dampers | Fire Retardent / Control Dampers
[29 empty] | Ducting | Fresh Air |  |  |  |  | Exhaust
[29 empty] | Sft | 20 Micron | 10 Micron | 5 Micron | 1 Micron | 0.3 Micron | 20 Micron
AHU - 1 Air-Conditioning System (DX)
| CLASS | Class100K | CFM | 15750 | AC Load | 56 | Nos. | 1 | 867500 | 867500 |  |  |  | 867500 | 625 | 410140.9375 | 235200 | 15000 | 77950 | 129150 | 710 | 710 | 0 | 15000 | 6 | 6 | 36 | 150 | 6000 | 0 | 36 | 36 | 36 | 0 | FALSE | 31.5 | 14.3182
| AHU(W) | 2050 | AHU(H) | 2050 | AHU(L) | 5900
| Blower | 710 | Static Pr | 125 | Motor Hp | 20
| Coil Rows | 8 | Coil Head Type | Distributor | Coil Size hxw in mm | 1293 h x 1650 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 6 | 6
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 610 | 150 | 9
| 5µ | 610 | 610 | 300 | 9
| 1µ | 610 | 610 | 300 | 9
| 0 | 0 | 0 | 0 | 0
| EXHAUST | AHU - 1 Air-Conditioning System (DX)
| No. of Filtr. Stages | 1 | CFM | 0 | Filter Ratings | 20µ | Nos. | 1 | 406750 | 406750
| AHU(W) | 2050 | AHU(H) | 2050 | AHU(L) | 2400
| Blower | 200 | Static Pr | 50 | Motor Hp | 1
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos | [8 empty] | 406750 | 375 | 130280.0625 | 235200 | 5000 | 17150 | 19050 | 200 | 0 | 0 | 10000 | 12 | 12 | 144 | 150 | 0 | 0 | 0 | FALSE | 0 | 0 | 0 | 0 | 0
|  | 6 | 6
| 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0
AHU - 2 Air-Conditioning System (DX)
| CLASS | ISO 6 | CFM | 48500 | AC Load | 124.5 | Nos. | 1 | 1911500 | 1911500 |  |  |  | 1911500 | 625 | 883396 | 522900 | 25000 | 0 | 480000 | 1200 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 10500 | 0 | 36 | 36 | 36 | 0 |  | 97 | 44.0909
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1200 | Static Pr | 150 | Motor Hp | 75
| Coil Rows | 4 | Coil Head Type | Distributor | Coil Size hxw in mm | 2635 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 4 Air-Conditioning System (Chilled Water)
| CLASS | GRADE A | CFM | 47000 | AC Load | 159 | Nos. | 1 | 2179000 | 2179000 |  |  |  | 2179000 | 625 | 1006060 | 667800 | 25000 | 0 | 480000 | 1200 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 10300 | 0 | 36 | 36 | 36 | 36 |  | 94 | 42.7273
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 7000
| Blower | 1200 | Static Pr | 150 | Motor Hp | 75
| Coil Rows | 6 | Coil Head Type | Header | Coil Size hxw in mm | 2244 h x 3600 w
| No. of Filtr. Stages | 4 | Filter Ratings | 10µ, 5µ, 1µ & 0.3µ (HEPA Plenum Fitted 95% eff.)
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0.3µ 95% Eff. HEPA Filetr | 610 | 915 | 300 | 6
AHU - 5 Air-Conditioning System (DX)
| CLASS | 10K | CFM | 36500 | AC Load | 94 | Nos. | 1 | 1784750 | 1784750 |  |  |  | 1784750 | 625 | 717692 | 394800 | 20000 | 286500 | 365580 | 1120 | 0 | 0 | 20000 | 10 | 8 | 80 | 150 | 9100 | 0 | 36 | 36 | 36 | 0 |  | 73 | 33.1818
| AHU(W) | 3600 | AHU(H) | 2900 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 50
| Coil Rows | 4 | Coil Head Type | Distributor | Coil Size hxw in mm | 2238 h x 3200 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 10 | 8
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 6 Air-Conditioning System (Chilled Water)
| CLASS | NC | CFM | 27500 | AC Load | 74.5 | Nos. | 1 | 1414750 | 1414750 |  |  |  | 1414750 | 625 | 622129.75 | 312900 | 20000 | 178900 | 280680 | 1000 | 1000 | 0 | 20000 | 8 | 8 | 64 | 150 | 7900 | 0 | 36 | 36 | 36 | 0 |  | 55 | 25
| AHU(W) | 2900 | AHU(H) | 2900 | AHU(L) | 5800
| Blower | 1000 | Static Pr | 150 | Motor Hp | 40
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2271 h x 2500 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 8 | 8
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 7 Air-Conditioning System (Chilled Water)
| CLASS | 5 Micron | CFM | 28250 | AC Load | 98 | Nos. | 1 | 1529000 | 1529000 |  |  |  | 1529000 | 625 | 637731.75 | 411600 | 20000 | 178900 | 280680 | 1000 | 1000 | 0 | 20000 | 8 | 8 | 64 | 150 | 8000 | 0 | 36 | 36 | 36 | 0 |  | 56.5 | 25.6818
| AHU(W) | 2900 | AHU(H) | 2900 | AHU(L) | 6000
| Blower | 1000 | Static Pr | 150 | Motor Hp | 40
| Coil Rows | 6 | Coil Head Type | Header | Coil Size hxw in mm | 1991 h x 2500 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 8 | 8
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 8 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 9 Air-Conditioning System (DX)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 159 | Nos. | 1 | 2282750 | 2282750 |  |  |  | 2282750 | 625 | 883396 | 667800 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Distributor | Coil Size hxw in mm | 3366 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 10 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 11 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 12 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 13 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 14 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 15 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 15 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 16 Ventilation System ( SUPPLY )
| CLASS | ISO 6 | CFM | 20000 | AC Load | 0 | Nos. | 1 | 749500 | 749500 |  |  |  | 749500 | 375 | 401361.45 | 0 | 20000 | 119650 | 208320 | 800 | 800 | 0 | 20000 | 8 | 8 | 64 | 150 | 6800 | 36 | 36 | 36 | 36 | 0 |  | 40 | 18.1818
| AHU(W) | 2900 | AHU(H) | 2900 | AHU(L) | 6400
| Blower | 800 | Static Pr | 150 | Motor Hp | 30
| Coil Rows | Amb | Coil Head Type | Amb | Coil Size hxw in mm | 0
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 8 | 8
| 20µ | 610 | 915 | 100 | 6
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 19 Air-Conditioning System (Chilled Water)
| CLASS | ISO 6 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
AHU - 20 Air-Conditioning System (Chilled Water)
| CLASS | ISO 5 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2173000 | 2173000 |  |  |  | 2173000 | 625 | 985616 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 36 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 6800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 4 | Filter Ratings | 10µ, 5µ, 1µ & 0.3µ (HEPA Plenum Fitted 95% eff.)
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0.3µ 95% Eff. HEPA Filetr | 610 | 915 | 300 | 6
AHU - 21 Air-Conditioning System (Chilled Water)
| CLASS | ISO 7 | CFM | 42500 | AC Load | 108.5 | Nos. | 1 | 2070750 | 2070750 |  |  |  | 2070750 | 625 | 883396 | 455700 | 25000 | 286500 | 420000 | 1120 | 0 | 0 | 10000 | 12 | 10 | 120 | 150 | 9800 | 0 | 36 | 36 | 36 | 0 |  | 85 | 38.6364
| AHU(W) | 4000 | AHU(H) | 3600 | AHU(L) | 5800
| Blower | 1120 | Static Pr | 150 | Motor Hp | 60
| Coil Rows | 4 | Coil Head Type | Header | Coil Size hxw in mm | 2297 h x 3600 w
| No. of Filtr. Stages | 3 | Filter Ratings | 10µ, 5µ & 1µ
Filters Size and Quantity for mentioned ratings
| Filter Rating | Width mm | Height mm | Depth mm | Filter Qty Nos
|  | 12 | 10
| 0 | 0 | 0 | 0 | 0
| 10µ | 610 | 915 | 150 | 6
| 5µ | 610 | 915 | 300 | 6
| 1µ | 610 | 915 | 300 | 6
| 0 | 0 | 0 | 0 | 0
B | NC Areas. ( 5 MICRON AC SUPPLY) ( PBC Block)
Double Skin AHU made out of Al. Hollow Section and 24 G GI Panels 25 mm thick duly filled with PUF with provision for Filter sections of 20 micron Fresh air, 10 micron Prefilter , 5 micron fine filtration, 1 micron Superfine Filtration, and 0.3 micron 95% HEPA Filter Section , fan section with backward curved centrifugal fan of 110 mm static pressure (Kruger Make) with V-Belt drive arrangement and access doors where ever necessary with FLP Motor (Crompton Make) of following capacities.
| Width | Height | Length | Cfm | Blower length | Filtrat. Length | [7 empty] | 679400
VSU - 001 | 1750 | 1550 | 7100 | 9000 | 1800 | 3800 | Nos. | 1 | 491400 | 491400 | 54600 | 54600 | 546000 | 546000 | 625 | 369858.1875 | 0 | 10000 | 45650 | 120420 | 560 | 560 | 0 | 10000 | 5 | 4 | 20 | 150 | 4500 | 20 | 20 | 20 | 20 | 20 |  | 18 | 8.1818
| 560 | 12.5 | 0 | 1200 | 5 | 0
| BDB | Motor | TR | Coil Depth | Filtrat. Stages | Coil Rows | [7 empty] | 0
C | NC Areas. ( 5 MICRON AC SUPPLY)
Double Skin AHU made out of Al. Hollow Section and 24 G GI Panels 25 mm thick duly filled with PUF with provision for Filter sections of 20 micron Fresh air, 10 micron Prefilter , 5 micron fine filtration, fan section with backward curved centrifugal fan of 90 mm static pressure (Kruger Make) with V-Belt drive arrangement and access doors where ever necessary with FLP Motor (Crompton Make) of following capacities.
PBC Block
| Width | Height | Length | Cfm | Blower length | Filtrat. Length
FAM - 001 | 950 | 950 | 5400 | 1850 | 1600 | 2300 | Nos. | 1 | 185625 | 185625 | 20625 | 20625 | 206250 | 206250 | 625 | 156204.9375 | 0 | 5000 | 18900 | 26100 | 250 | 450 | 250 | 5000 | 2 | 2 | 4 | 150 | 2100 | 4 | 4 | 4 | 4 |  |  | 3.7 | 1.6818
| 250 | 1.5 | 0 | 1200 | 3 | 0
FAM - 002 | 950 | 950 | 5400 | 1950 | 1600 | 2300 | Nos. | 1 | 185625 | 185625 | 20625 | 20625 | 206250 | 206250 | 625 | 156204.9375 | 0 | 5000 | 18900 | 26100 | 250 | 450 | 250 | 5000 | 2 | 2 | 4 | 150 | 2100 | 4 | 4 | 4 | 4 |  |  | 3.9 | 1.7727
| 250 | 1.5 | 0 | 1200 | 3 | 0
| BDB | Motor | TR | Coil Depth | Filtrat. Stages | Coil Rows | [7 empty] | 453500
VSU - 002 | 1550 | 1100 | 5450 | 3900 | 1650 | 2300 | Nos. | 1 | 273825 | 273825 | 30425 | 30425 | 304250 | 304250 | 625 | 228650 | 0 | 8000 | 21900 | 45600 | 355 | 450 | 355 | 8000 | 4 | 2 | 8 | 150 | 3000 | 8 | 8 | 8 | 8 |  |  | 7.8 | 3.5455
| 355 | 5 | 0 | 1200 | 3 | 0
VSU - 003 | 1550 | 1250 | 5450 | 4450 | 1650 | 2300 | Nos. | 1 | 290250 | 290250 | 32250 | 32250 | 322500 | 322500 | 625 | 244336.0625 | 0 | 8000 | 24400 | 45600 | 400 | 450 | 400 | 8000 | 4 | 3 | 12 | 150 | 3200 | 12 | 12 | 12 | 12 |  |  | 8.9 | 4.0455
| 400 | 5 | 0 | 1200 | 3 | 0
PP Block
VSU - 004 | 1750 | 1550 | 5600 | 9000 | 1800 | 2300 | Nos. | 2 | 364275 | 728550 | 40475 | 80950 | 404750 | 404750 | 625 | 303280.6875 | 0 | 10000 | 45650 | 45600 | 560 | 560 | 0 | 10000 | 5 | 4 | 20 | 150 | 9000 | 20 | 20 | 20 | 20 |  |  | 18 | 8.1818
| 560 | 5 | 0 | 1200 | 3 | 0
VSU - 005 | 1750 | 1550 | 5600 | 10000 | 1800 | 2300 | Nos. | 2 | 364275 | 728550 | 40475 | 80950 | 404750 | 404750 | 625 | 303280.6875 | 0 | 10000 | 45650 | 45600 | 560 | 560 | 0 | 10000 | 5 | 4 | 20 | 150 | 9500 | 20 | 20 | 20 | 20 |  |  | 20 | 9.0909
| 560 | 5 | 0 | 1200 | 3 | 0
D | EXHAUST SYSTEM ( VENTILATION )
Single Skin AHU made out of Al. Hollow Section and 18 G GI Panels 25 mm thick with provision for Filter sections of 20 Micron exhaust air, fan section with backward curved centrifugal fan of 50 mm static pressure (Kruger Make) with V-Belt drive arrangement and access doors where ever necessary with FLP Motor (Crompton Make).
PBC Block
| Width | Height | Length | Cfm | Blower length | Filtrat. Length
FEM - 001 | 950 | 950 | 2100 | 1750 | 1600 | 500 | Nos. | 1 | 91575 | 91575 | 10175 | 10175 | 101750 | 101750 | 450 | 51748.875 | 0 | 5000 | 18900 | 26100 | 250 | 450 | 250 | 5000 | 2 | 2 | 4 | 150 | 2000 | [5 empty] | 4 | 2.6923 | 1.5909
| 250 | 1.5 | 0 | 0 | 1 | 0
FEM - 002 | 950 | 950 | 2100 | 1825 | 1600 | 500 | Nos. | 1 | 91575 | 91575 | 10175 | 10175 | 101750 | 101750 | 450 | 51748.875 | 0 | 5000 | 18900 | 26100 | 250 | 450 | 250 | 5000 | 2 | 2 | 4 | 150 | 2100 | [5 empty] | 4 | 2.8077 | 1.6591
| 250 | 1.5 | 0 | 0 | 1 | 0
| BDB | Motor | TR | Coil Depth | Filtrat. Stages | Coil Rows
VEU - 001 | 1750 | 1550 | 2300 | 8575 | 1800 | 500 | Nos. | 1 | 192825 | 192825 | 21425 | 21425 | 214250 | 214250 | 450 | 112903.335 | 0 | 10000 | 45650 | 45600 | 560 | 560 | 0 | 10000 | 5 | 4 | 20 | 150 | 4400 | [5 empty] | 20 | 13.1923 | 7.7955
| 560 | 5 | 0 | 0 | 1 | 0
VEU - 002 | 1550 | 1100 | 2150 | 3700 | 1650 | 500 | Nos. | 1 | 131400 | 131400 | 14600 | 14600 | 146000 | 146000 | 450 | 79941.42 | 0 | 8000 | 21900 | 36000 | 355 | 450 | 355 | 8000 | 4 | 2 | 8 | 150 | 2900 | [5 empty] | 8 | 5.6923 | 3.3636
| 355 | 3 | 0 | 0 | 1 | 0
VEU - 003 | 1550 | 1250 | 2150 | 4200 | 1650 | 500 | Nos. | 1 | 137250 | 137250 | 15250 | 15250 | 152500 | 152500 | 450 | 86441.805 | 0 | 8000 | 21900 | 36000 | 355 | 450 | 355 | 8000 | 4 | 3 | 12 | 150 | 3100 | [5 empty] | 12 | 6.4615 | 3.8182
| 355 | 3 | 0 | 0 | 1 | 0
| BDB | Motor | TR | Coil Depth | Filtrat. Stages | Coil Rows
PP Block
VEU - 004 | 1750 | 1550 | 2200 | 8250 | 1700 | 500 | Nos. | 2 | 182700 | 365400 | 20300 | 40600 | 203000 | 203000 | 450 | 109707.615 | 0 | 10000 | 37450 | 45600 | 500 | 500 | 0 | 10000 | 5 | 4 | 20 | 150 | 8700 | [5 empty] | 20 | 12.6923 | 7.5
| 500 | 5 | 0 | 0 | 1 | 0
VEU - 005 | 1750 | 1550 | 2300 | 9250 | 1800 | 500 | Nos. | 2 | 192825 | 385650 | 21425 | 42850 | 214250 | 214250 | 450 | 112903.335 | 0 | 10000 | 45650 | 45600 | 560 | 560 | 0 | 10000 | 5 | 4 | 20 | 150 | 9200 | [5 empty] | 20 | 14.2308 | 8.4091
| 560 | 5 | 0 | 0 | 1 | 0
PBC Block
Ex. 1 Modules | 600 | 600 | 2100 | 575 | 1600 | 500 | Nos. | 4 | 64575 | 258300 | 7175 | 28700 | 71750 | 71750 | 450 | 29633.04 | 0 | 5000 | 17150 | 19920 | 200 | 450 | 200 | 5000 | 1 | 1 | 1 | 150 | 4600 | [5 empty] | 1 | 0.88462 | 0.52273
|  | 0.5 | 0 | 0 | 1 | 0
Ex. 2 Modules | 600 | 600 | 2100 | 300 | 1600 | 500 | Nos. | 1 | 64575 | 64575 | 7175 | 7175 | 71750 | 71750 | 450 | 29633.04 | 0 | 5000 | 17150 | 19920 | 200 | 450 | 200 | 5000 | 1 | 1 | 1 | 150 | 900 | [5 empty] | 1 | 0.46154 | 0.27273
|  | 0.5 | 0 | 0 | 1 | 0
PP Block
Ex. 2 Modules | 600 | 600 | 2100 | 300 | 1600 | 500 | Nos. | 2 | 64575 | 129150 | 7175 | 14350 | 71750 | 71750 | 450 | 29633.04 | 0 | 5000 | 17150 | 19920 | 200 | 450 | 200 | 5000 | 1 | 1 | 1 | 150 | 1700 | [5 empty] | 1 | 0.46154 | 0.27273
|  | 0.5 | 0 | 0 | 1 | 0
II | AIR CIRCULATION SYSTEM | [25 empty] | 2300 |  | 224100
Ducting Works
1 | 24 G GI ducting with MS angle joints duly with rubber | [5 empty] | Sft | 89000 | 116.2 | 10341800 | 11.62 | 1034180 | 116.2 | 116.2 | [15 empty] | 130 | 780 | 780 | 780 | 100 | 100 | 1580 | 730
gasket joined with GI plated 06 mm Nut bolts and
supported by 8 mm GI threaded rods and Sealed
duly with Silicon Sealant on joints
2 | 22 G GI ducting with MS angle joints duly with rubber | [5 empty] | Sft | 78500 | 125.5 | 9851750 | 12.55 | 985175 | 125.5 | 125.5
gasket joined with GI plated 06 mm Nut bolts and
supported by 8 mm GI threaded rods and Sealed
duly with Silicon Sealant on joints
3 | 20 G GI ducting with MS angle joints duly with rubber | [5 empty] | Sft | 59500 | 134.8 | 8020600 | 13.48 | 802060 | 134.8 | 134.8 | [15 empty] | 20 micr | 10 micr | 5 micr | 1 micr | 0.3 micr | 20 micr Exhaust | Al Dampers | Al Dampers
gasket joined with GI plated 06 mm Nut bolts and
supported by 8 mm GI threaded rods and Sealed
duly with Silicon Sealant on joints
Insulation Works
4 | 13 mm thick Cross linked closedcell foil faced | [5 empty] | Sft | 112500 | 72 | 8100000 | 7.2 | 810000 | 72 | 72
insulation for return air with taped joints.
5 | 19 mm thick Cross linked closedcell foil faced | [5 empty] | Sft | 112500 | 80 | 9000000 | 8 | 900000 | 80 | 80
insulation for Supply air with taped joints.
Grills / Diffusers / Perforated
6 | SS 316. Perforated Grills duly boughed | [5 empty] | Sft | 10740 | 1100 | 11814000 | 110 | 1181400 | 1100 | 1100
for Supply & return air in 100K & NC areas
Fire Resistant / Retardant / Control Dampers
7 | Fire Resistant Opposite Blade type Volume control | [5 empty] | Sft | 730 | 1400 | 1022000 | 140 | 102200 | 1400 | 1400
dampers at AHU made out of 18 GI duly epoxy
powder coated / PU painted with fusible link.
Volume Control Dampers
7 | Opposite Blade type Volume control Dampers for Air | [5 empty] | Sft | 220 | 750 | 165000 | 75 | 16500 | 750 | 750
distribution control in ducts made out of 20 GI
duly Epoxy powder coated / PU painted.
8 | Gear type control Dampers for distribution | [5 empty] | Sft | 2310 | 1500 | 3465000 | 150 | 346500 | 1500 | 1500
AHU's for Supply , Fresh air , Retrun Air & Exhaust Air.
Terminal Filtration \ Grill Modules
9 | Supply, return & Exhaust Air filter Modules for | [5 empty] | Sft | 8936 | 2750 | 24574000 | 275 | 2457400 | 2750 | 2750
fixing Terminal Filters and grills duly epoxy powder coated made
out of 18/20 G CRCA for 100 K,5 & 20 micron
areas. with Gear Mechanism.
10 | Flexible canvas connections for AHU Inlets, Outlets, fresh air Terminal Grill | [5 empty] | Sft | 9850 | 150 | 1477500 | 15 | 147750 | 150 | 150
/Filter Modules , Terminals , Blowers, and plenum connections & others if any.
III | AIR FILTRATION SYSTEM
1 | 10 micron filters made out of HLP media with | [5 empty] | Sft | 780 | 550 | 429000 | 55 | 42900 | 550 | 550
one side HDPE & other side Al. expanded mesh of
efficiency 95% (150mm)
2 | 5 micron filters made out of SNPF media with | [5 empty] | Sft | 780 | 750 | 585000 | 75 | 58500 | 750 | 750
one side HDPE & other side Al. expanded mesh of
efficiency 99%(300 mm) ( 150 GSM )
3 | 1 micron filters made out of SNPF media with | [5 empty] | Sft | 780 | 850 | 663000 | 85 | 66300 | 850 | 850
one side HDPE & other side Al. expanded mesh of
efficiency 99.9%(300 mm)( 200 GSM )
4 | 20 micron filters made out of HDPE media with | [5 empty] | Sft | 130 | 500 | 65000 | 50 | 6500 | 500 | 500
one side HDPE & other side Al. expanded mesh of
efficiency 90%(150 mm) for fresh air supply
5 | 20 micron filters made out of HDPE media with | [5 empty] | Sft | 100 | 500 | 50000 | 50 | 5000 | 500 | 500
one side HDPE & other side Al. expanded mesh of
efficiency 90%(150 mm) for Exhaust air.
6 | 0.3 micron (HEPA) filters made out of | [5 empty] | Sft | 100 | 3250 | 325000 | 975 | 97500 | 3250 | 3250
imported lydall media of efficiency 95% for ISO 8 / 100K / ISO 5, 100 Areas.
7 | 10 micron filters made out of HLP media with | [5 empty] | Sft | 4500 | 400 | 1800000 | 40 | 180000 | 400 | 400
one side HDPE & other side Al. expanded mesh of
efficiency 95% (50mm thick)for Return air in Class
100K & 5 Micron Areas.
8 | 5 micron filters made out of SNPF media | [5 empty] | Sft | 4500 | 450 | 2025000 | 45 | 202500 | 450 | 450
with one side HDPE & other side Al. expanded mesh
of efficiency 95% (50mm thick) for Supply air in
Class 100K & 5 Micron Areas.
9 | 0.3 micron (HEPA) filters made out of imported lydall media of 300 mm Thick | [5 empty] | Sft | 350 | 3250 | 1137500 | 325 | 113750 | 450 | 3250
efficiency 99.95%/99.97%/99.997% for 10K or ISO 7 Area.
10 | 0.3 micron (HEPA) filters made out of imported lydall media of 150 mm Thick | [5 empty] | Sft | 3950 | 3250 | 12837500 | 325 | 1283750 | 450 | 3250
efficiency 99.995%/99.997% for 1K or Class 100 or ISO 6 or ISO 5 Area.
11 | 0.12 micron (ULPA) filters made out of imported lydall media of 65/80 mm Thick | [5 empty] | Sft | 950 | 3250 | 3087500 | 325 | 308750 | 450 | 3250
efficiency 99.9997% / 99.9999% for Class 100 / Class 10 / Class 1/ ISO 5 / ISO 4 / ISO 3 Area.
IV | PRESSURE MONITORING SYSTEM
1 | 0-10 mm DWYER make Magnehelic Guages | [5 empty] | Nos. | 320 | 6750 | 2160000 | 750 | 240000 | 7500 | 7500 | =COUNTIFS('BOD-Cold & Amb.'!istext(N10:N225)) | 176
for Room pressures indication
2 | 0-50 mm DWYER make Magnehelic Guages | [5 empty] | Nos. | 59 | 6750 | 398250 | 750 | 44250 | 7500 | 7500
for filter pressure drop indication in AHU's
3 | SS 304 Individual Magnehelic gauge housing | [5 empty] | Nos. | 379 | 3600 | 1364400 | 400 | 151600 | 4000 | 4000
| with sensor | [12 empty] | 4000
4 | SMART PROCESS SCANNERS with in built Sensor | [5 empty] | Nos. | 304 | 67500 | 20520000 | 7500 | 2280000 | 75000 | 75000
Make:POLMON
Specifications:
In built :RH,Temperature & DP
Output Type-Modbus
X-Future Use
Display: RH, TEMP. and DP
Set point for each parameter (Hi/Low).
Display Blinking on Violation (Optional Buzzer Indication).
Programmable Damping/ Filter constant for each parameter.
Independent Displays for each parameter.
Diagnostic messages for each parameter.
Fully Differential Inputs.
Optically Isolated communication port.
Programmable Baud Rate Selection 1200/ 9600/ 19.2KB/ 38.4KB.
Power Supply: 24 VAC
SS face plate
Mounting: Modular Wall Mounting
5 | DP TRANSMITTERS FOR CLEAN ROOMS | [5 empty] | Nos. | 304 | 45000 | 0 | 5000 | 0 | 50000 | 50000
Make:POLMON
Local Display:required
Specifications:
1-Face Plate Of Material- SS
X- 0-12mm WC
Lifetime Stability of -/+0.5% F.S.O
No Calibration or recalibration necessary for the life of the device
Standard 2-Year warranty
Accuracy:1% on FSO
Output:4-20mA
Calibrated to NIST-Traceable standards
Media compatability:clean,dry inert,non-ferrous gases
6 | DP MOUNTING BOX WITH ACCESSORIES | [5 empty] | Nos. | 304 | 2700 | 820800 | 300 | 91200 | 3000 | 3000
1-Type Of Material-SS-304
1-Depth-1-50mm
V | VALIDATION
1 | Commissioning & Validation of Total Clean Room | [5 empty] | L/s. | 1 | 0 | 0 | 600000 | 600000 | 600000 | 600000
| (Air Balancing,Temp., Pressure Balancing, Particle | [10 empty] | . |  | .
Count, HEPA Integrity Test (D.O.P), recovery Test
with DQ/IQ/OQ/PQ reports)
[10 empty] | 176837125 |  | 15081390
191918515
Terms & Conditions :
1 | The above prices are inclusive of Packing, Forwarding, erection & Commissioning of the system.
2 | Transportation Charges & Unloading Charges extra at actuals in client's scope.
3 | Accomodation at Site Shall be provided for 20 - 25 Persons at the cost of Client.
4 | GST@18% extra
7 | However any tax variations at the time of delivery shall be applicable as per actuals.
8 | All civil, False Ceiling works & electrical cabling, starters, Panel Boards etc. will be in client's scope.
9 | All electrical cable connections shall be connected to AHU motors at the installated Areas.
10 | Ducting, Dampers, Insulation,Grills & terminal modules with Filters are tentative and will be charged as per actuals.
11 | Scaffoldings or support structures required if any shall be in clients scope
12 | All heat loads are based on calculations as per oral references, if any changes as per practical site conditions
shall be reworked along with prices.
13 | All test Certificates along with Calibration & Traceable certificates will be provided.
14 | All detailed equipment / duct drawings will be submitted for approvals against your W.O. / LOI along with Advance.
15 | Chilled water/ DX connections along with all piping & controls with accessories does not include in our scope.
Along with Condensing Units / Chiller Plant.
16 | Dehumidifier is necessary to control humidity anything below 55+/-5% along with prec-cooling of fresh Air.
17 | Drain water connections along with all piping & accessories does not include in our scope.
18 | All equipments are guaranteed against any manufacturing defects for a period of 12 months from the date of
Commissioning or 15 months from the date of supply which ever is earliest.
18 | DELIVERY: 06-08 months from the date of Confirmed P.O. & ADVANCE
( From the date of approval of Layout Drawings, Duct routing Drawings, AHU's drawings etc.)
Installation within 10 months, Commissioning - 1 month, Documentation ( DQ/IQ/OQ/PQ) - 1 month
19 | Payment : Supply : 50 % advance, 50 % against Proforma Invoice on Pro-rata Basis. Installation : 50% Advance,
balance against installation & commissioning.
20 | If Canteen facilities can be provided at your site work for 20-25 Persons to complete the work at a faster rate shall be helpful..
21 | Safe Working Place and material Storage place for & from our ---------------company shall be provided at Site at clients cost.
22 | Lifting, Shifting, Positioning of all Heavy and necessary material at site is in Client's Scope.
23 | Offer Validity : 15 days.
we hope the above will meet your requirement and please feel free to contact us for any Techno-commercial
discussions in this regard.

## HVAC WORKS
SCHEDULE OF QUANTITIES
(VARIABLE REFRIGERANT FLOW SYSTEM)
SUMMARY OF COSTS
ITEM | DESCRIPTION |  |  |  | AMOUNT
1 | EQUIPMENT |  |  |  | 0
2 | AIR DISTRIBUTION |  |  |  | 0
3 | INSULATION |  |  |  | 0
4 | ELECTRICAL WORK |  |  |  | 0
| TOTAL |  |  |  | 0
* All Taxes & Duties shall be extra as applicable.
ITEM | DESCRIPTION | UNIT | QTY. | RATE | AMOUNT
1.0 | EQUIPMENT
1.1 | VRF SYSTEM
1.1.1 | VRF OUTDOOR UNIT
Supply, Installation, Testing and Commissioning of air cooled variable refrigerant flow modular type condensing units with anti-corrosion treatment, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas (R-410a), lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling & heating mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. All the units shall be provided with built-in microprocessor control panel, for automatic operation and capacity control. Machines shall be suitable for working with BMS system.VRV/VRF system shall have auto Restart function i.e. In case of power failure, units should restart automatic when power resume.The VRV/VRF system shall have free phase technology, which shall correct phases automatically in case of phase reversal.The condensing units shall be suitable for operation on 415 ± 10% volts, 50Hz, 3 phase AC power supply and the condensing units shall be of following capacities:
The Selected VRF Unit must have a COP of at least 3.6 under AHRI conditions.
| i. 38 HP Nominal capacity | No | 1 |  | 0
| ii. 32 HP Nominal capacity | No | 1 |  | 0
| iii. 20 HP Nominal capacity | No | 6 |  | 0
| iv. 16 HP Nominal capacity | No | 2 |  | 0
| v. 12 HP Nominal capacity | No | 1 |  | 0
| vi. 8 HP Nominal capacity | No | 2 |  | 0
| vii. 6 HP Nominal capacity | No | 3 |  | 0
NOTES:
1. The above mentioned outdoor units shall be provided with anti corrossion treatment (preferably from factory). The quoted price shall be inclusive of same.
b. The above mentioned outdoor units should capable to work upto 50°C Ambient Temperature.
1.1.2 | VRF INDOOR UNITS
Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling & heating mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 ±6% volts, 50Hz, 1 phase AC power supply. Ductable indoor units shall be suitable to handle extent of ductwork as shown in the design drawings and dehumidified air quantity as mentioned in the heat load summary sheet under "Special Conditions". The indoor unit shall be complete with pre filter as per requirement The indoor units shall be of following capacities:
The Selected VRF Unit must have a COP of at least 3.6 under AHRI conditions.
a. | Ceiling Mounted Ductable Indoor Units
(With corded control)
| i. 8.0 TR nominal capacity | No | 1 |  | 0
| ii. 6.4 TR nominal capacity | No | 5 |  | 0
| iii. 5.4 TR nominal capacity | No | 4 |  | 0
| iv. 4.5 TR nominal capacity | No | 6 |  | 0
| v. 2.5 TR nominal capacity | No | 1 |  | 0
| vi. 2.0 TR nominal capacity | No | 1 |  | 0
| vi. 1.3 TR nominal capacity | No | -- | Quote Rate
| vii. 1 TR nominal capacity | No | -- | Quote Rate
Note: For the above mentioned medium static units, the quoted price should be inclusive of room thermostats.
b. | Round Flow 4 Way Cassette Units
| i. 3.2 TR nominal capacity | No | 6 |  | 0
| ii. 2.5 TR nominal capacity | No | 1 |  | 0
| iii. 1.6 TR nominal capacity | No | 5 |  | 0
| iii. 1.3 TR nominal capacity | No | 7 |  | 0
| iv. 1 TR nominal capacity | No | 11 |  | 0
| v. 0.8TR nominal capacity | No | 83 |  | 0
c. | Hi-Wall Units (with drain pump for critical rooms)
| i. 2.0 TR nominal capacity | No | 4 |  | 0
| ii. 1.6 TR nominal capacity | No | 5 |  | 0
| iii. 1.3 TR nominal capacity | No | 3 |  | 0
| iv. 1 TR nominal capacity | No | 1 |  | 0
| v. 0.6 TR nominal capacity | No | 1 |  | 0
NOTE:
The above mentioned outdoor units shall be provided with anti-corrosion treatment from factory. The quoted price shall be inclusive of same.
1.2 | DX TYPE TREATED FRESH AIR UNITS -- TFAUs
(Floor Mounted.)
Supply, Installation, Testing and Commissioning of double skin sheet metal sectionalised construction Treated Fresh air units, double skin panels with 46mm thick injected PUF of density not less than 40Kg/CuM with thermal break profile. The treated fresh units shall be complete with pre-filter (MERV-8), 300mm thick fine filter (MERV 13) multi rows deep DX cooling coil of copper tube and aluminium fin construction (with 100mm gap between two sets of three rows deep cooling coils), fan section complete with floor standing backward curved DIDW centrifugal fan with MCB/ MCCB of appropriate rating with cable termination box, belt drive package, IE-03 squirrel cage induction motor, insulated SS drain pan, vibration isolation pads etc. all complete as per the specifications. TFA shall be selected for a maximum face velocity of 500 FPM (2.5MPS). Fan outlet velocity shall not exceed 2000 FPM (10.1 MPS). The dB level shall not be more than 60 to 65 @1 Mtr.The unit/s shall be be provided with factory fabricated plenum on filter side, with access doors /panels, for duct termination. The unit shall be supplied with electronic expansion valve/s (Dx), thermostats, control wiring & all accessories as required for completing installation. AHUs shall be of following design parameters:
Unit shall be suitable for VFDs operation.
TFA Capacity SP No. of Motor Ref. Calculated
No. (Cfm) (mm WG) Rows Rating (HP) Load (TR)
| TFA- 1000 50 6 2.0 6.8 | No | -- | Quote Rate
1.3 | COPPER PIPING
Supply, Installation, Testing & Commissioning of high pressure copper refrigerant piping suitable for R 410a refrigerant of suitable size as required and duly insulated with 19mm/13mm thick EPDM closed cell elastomeric insulation with class "O" fire rating in tubing form inclusive of glass cloth and UV treatment. All insulation joints shall have tape of same material with equivalent fire rating as the insulation. External Refrigerant piping and refrigerant piping in exposed ceiling area shall be laid on GI covered cable trays. Piping inside occupied spaces within false ceiling shall be supported using GI ladder type cable trays. Entire refrigerant piping work shall be carried out in accordance with the specifications and should have anti corrosion treatment. Piping shall be of following sizes:
Pipe Size Min. Wall Insulation
Size (O.D.) Thickness Thickness
a. | 41.3 mm 1.43 mm 19 mm | RM | 30 |  | 0
b. | 34.9 mm 1.21 mm 19 mm | RM | 30 |  | 0
c. | 28.6 mm 0.99 mm 19 mm | RM | 220 |  | 0
d. | 25.4 mm 0.80 mm 13 mm | RM | -- |  | Quote Rate
e. | 22.2 mm 0.80 mm 13 mm | RM | 120 |  | 0
f. | 19.1 mm 0.80 mm 13 mm | RM | 250 |  | 0
g. | 15.9 mm 1.00 mm 13 mm | RM | 280 |  | 0
h. | 12.7 mm 0.80 mm 13 mm | RM | 640 |  | 0
i. | 9.5 mm 0.80 mm 13 mm | RM | 360 |  | 0
j. | 6.4 mm 0.80 mm 13 mm | RM | 580 |  | 0
1.4 | FITTINGS
Supply, Installation, Testing and Commissioning of following imported fittings to be provided in refrigerant pipe line. Material of construction for fittings shall be similar to refrigerant piping.
a. | Y- joints for refrigerant piping (pair). | No | 129 |  | 0
1.5 | Critical Room AC Panel (CRAP)
| Supply, Installation, Testing and Commissioning of Temerature & RH sensor with Display & hooter for all the technical rooms. | No | 7 |  | 0
1.6 | BMS INTERFACE/ CENTRALIZED CONTROLLER (TOUCHSCREEN TYPE)
| Supply, Installation, Testing & Commissioning of BMS compatible main centralised controller -I touch Manager (with Bacnet Module) as per specifications to hook up indoor/ outdoor units as mentioned above. The controller shall however be suitable for catering to all the indoor/ outdoor units for the complete project. Funtions of the centralized controller in brief shall include but not be limited to remote start/stop of units, temperature setpoint control, status monitoring etc. | NO | 1 |  | 0
1.7 | CONDENSATE DRAIN PUMP
Supply Installation, Testing and Commissioning of condensate drain pump with insulated sump having adequate provision for connections. It shall be provided with necessary controllers complete with control wiring in all respect as required and as per the specifications. The pumps shall be of following sizes:
| a. Hi-flow 2L | No | -- |  | Quote Rate
1.8 | Supply, Fabrication and Installation of MS frame using channels/angle iron sections as required for mounting of air cooled remote condenser/s in service areas or terrace level. The frame work shall be applied with red oxide primer and thereafter, two coats of enamel paint of approved colour. The general arrangement drawing for frame work shall be gotten approved from the Architects/ Structural Engineers prior to commencement of fabrication. | Kg | 1250 |  | 0
1.9 | Providing and fixing in position the following GI medium class pipes for condensate drain cut to required lengths & installed with all screwed joints and providing and fixing position the necessary elbows, tees & reducers.
| a. 32mm dia | RM | -- |  | Quote Rate
| b. 25mm dia | RM | -- |  | Quote Rate
1.1 | Providing, jointing and fixing of uPVC/ CPVC Condensate drain piping with all fittings conforming to IS: 15778:2007 of SDR 11 Grade. Fittings shall include all standard moulded fittings elbows, tees, couplers, reducers, unions, plugs, adaptors with brass threaded insertions and specials. The Solvent Cement for jointing shall be of make and grade as specified by the manufacturer of uPVC/ CPVC piping system. The installation shall be complete in all respects including cutting chases / holes in walls, slabs and making good, etc The entire uPVC/ CPVC piping system shall be installed, tested and commissioned following the recommendation of the manufacturer including provision of expansion loops. All pipework in shafts, ceiling voids and terrace shall be fixed on MS brackets and hangers with U-clamps made from 10 mm dia galvanised steel rod complete with nuts and washers. Cost for MS structural work for supports shall be included in the rates. All horizontal and vertical crossings of building structure (slabs, walls, beams, column etc), the space between pipe and the structure shall be made good and water tight with concrete.
The annular space between the pipe and the sleeves shall be sealed (upto a minimum depth 25 mm) with fire resistant acrylic based sealent of approved make and quality. The pipes shall be painted with two coats of synthetic enamel paint and painting with photoluminescent paint at suitable interval for identification of pipe lines.
| a. 40mm dia | RM | 250 |  | 0
| b. 32mm dia | RM | 310 |  | 0
| c. 25mm dia | RM | 350 |  | 0
1.11 | Extract Fan Sections
Supply, Installation, Testing and Commissioning of approved make fan section for extract air complete with backward curved DIDW centrifugal fan, MS base frame, IE-03 TEFC squirrel cage induction motor with class "F" insulation, drive package and vibration isolation arrangement including spring isolators, rubber grommets etc. as called for in working drawings & specifications.Fan section casing shall be of double skin sheet metal construction, double skin panels with 25mm thick injected PUF of density not less than 40 kg/CuM. Fan shall be suitable for operation on 415 ± 10% volts, 50 Hz 3 phase AC power supply. Fan outlet velocity shall not exceed 2000 FPM for FM Units & 1800 FPM for CS Units. Extract fan section shall be suitable for ceiling suspension/floor installation as shown in the design drawings. The fan characteristics shall be as follows:
Fan Capacity S.P Motor Type
No. (Cfm) (mmWG) Rating
(HP)
| EFS-1 6500 60 5 FM | No | -- |  | Quote Rate
| EFS-2 6200 60 5 FM | No | -- |  | Quote Rate
1.12 | INLINE FANS
Supply, Installation, Testing and Commissioning of circular/rectangular inline fans for exhaust air as shown on drawings, complete with sheet metal casing, direct driven centrifugal fan, motor with proper protection and inspection door,gravity louvers etc. as per the specifications. Fan should be suitable for operation on 415+10% volts, 50 Hz, three phase or 220±10 %, 50 Hz, single phase AC power supply as required. Single Phase inline fans shall be provided with speed regulators.
Fan shall be suitable for installation or as shown on drawings and shall be of following capacities:
Fan Capacity SP Electrical Type
No. (Cfm) (mmWG) Characteristics
| IF- 800 15 220V/1 Ph Circular | No | -- |  | Quote Rate
| IF- 100 15 220V/1 Ph Circular (Battery Room) | No | 6 |  | 0
1.13 | VARIABLE FREQUENCY DRIVES
Supply, Installation, Testing & Commissioning of variable frequency drives for following Air Handling Units/ Treated Fresh Air Units/Staircase Pressurization fans. Variable frequency drives shall be provided with necessary temperature/DP sensors and controllers complete with control wiring in all respect as required and as per the specifications. The drives shall be suitable for the following motor rating. VFDs shall be housed in AHU/TFA panels & in IP-55 Enclosure for Pressurization fans.
| i. 5 HP | No | -- |  | Quote Rate
| ii. 1 HP | No | -- |  | Quote Rate
1.14 | AIR CURTAIN
Supply , Installation and Testing of air curtains with noiseless dynamically balanced aluminium blowers, cleanable type pre-filters, motor & powder coated aluminium enclosure as per the specifications.
| a. 2 M long air curtain | No | -- |  | Quote Rate
| b. 1.8 M long air curtain | No | -- |  | Quote Rate
1.15 | AIR & SURFACE DISINFECTING OH RADICAL GENERATORS - DUCT MOUNTED
| Supply, Installation, Testing and commissioning of duct mounted Hydroxyl Radical Generators for Air & Surface disinfection for use within occupied building spaces. The device shall be compatible with 220 V + 10%, 50 Hz, Single Phase AC Power Supply. The unit shall be capable of producing human friendly Hydroxyl Radicals and Organic Oxidants and cater upto 3000 Square Feet of Area fed by a single supply air duct. OEM shall produce 13 week GLP toxicology report on the technology used in the device to support human safety claims. The unit shall be capable of reducing indoor air pollutants such as Viruses, Bacteria, Fungus, VOCs, and odors - the OEM must produce lab test reports from reputed international laboratories against at least 10 different types of pathogens. The OEM must also produce COVID-19 causing Coronavirus Reduction Test Reports from reputed International BSL3 Laboratory, with minimum reduction in virus load of 99% in 20 minutes or less in air, and in 60 mins or less on surfaces. The technology used in the device should have USFDA approval, and should have recommendation for use from DRDO/ ICMR in India for COVID-19. The quoted price shall be inclusive of power to be drawn to Hydroxyl Radical Generators from the nearby DB including but not limited to the following - power/ control cabling, MS conduiting, 6A DP MCB isolator, socket near the unit etc. so that these units only operate when the AHUs are in operation. Certifications shall be submitted along with the technical submitals, refer technical specififcations for required compliances. The Hydroxyl Radical Generators shall be suitable for the following area of treatment: | No | 13 |  | 0
TOTAL CARRIED TO SUMMARY (EQUIPMENT) Rs. |  |  |  |  | 0
2.0 | AIR DISTRIBUTION
2.1 | Ductwork
a. | Factory Fabricated Ductwork
Supply of factory fabricated dutwork, Installation and Testing of galvanised sheet metal ducts including elbows, turning vanes, fire retardant gaskets, TDF flanges, GI fully threaded rods, GI supports/hangers etc. in accordance with the approved shop drawings and specifications. The ducts shall be fabricated and installed in line with SMACNA standards.Galvanized sheet shall possess light coating of Zinc, generally 120gm/SqM of surface area.
| a. 1mm-500mm (26 gauge) GSS | SqM | 250 |  | 0
| b. 501mm-1050mm (26 gauge) GSS | SqM | 380 |  | 0
| c. 1051mm-1500mm (24 gauge) GSS | SqM | 170 |  | 0
| d. 1501mm-1800mm (22 gauge) GSS | SqM | 50 |  | 0
| e. 1801mm-2100mm (20 gauge) GSS | SqM | -- |  | Quote Rate
| f. 2101mm and above (18 gauge) GSS | SqM | -- |  | Quote Rate
b. | Conventional site fabricated ducts using Lock Forming Machines.
Supply, Fabrication, Installation and Testing of sheet metal ducts in accordance with the approved shop drawings and specifications. Ducts shall be fabricated using lock forming machine.Galvanized sheet shall possess light coating of Zinc, generally 120gm/SqM of surface area.
| a. 0.63mm (24 gauge) GSS | SqM | 50 |  | 0
| b. 0.8 mm (22 gauge) GSS | SqM | 50 |  | 0
| c. 1.0mm (20 gauge) GSS | SqM | -- |  | Quote Rate
| d. 1.25mm (18 gauge) GSS | SqM | -- |  | Quote Rate
c. | Supply, Fabrication, Installation & Testing of round sheet metal ducts in accordance with the approved shop drawings and specifications.
| a. 1.0mm (20 gauge) GSS | SqM | -- |  | Quote Rate
d | Supply, Fabrication, Installation and Testing of Powder Coated Eliptical sheet metal ducts in accordance with the approved shop drawings and specifications. All longitudinal and transverse joints should be fully applied with sealants.The joints shall be with least leak and shall be pressure tested. All ducts shall undergo deep cleaning process to remove construction dust prior to testing & commisioning.
| a. 1.0mm (20 gauge) GSS | SqM | 60 |  | 0
2.2 | Supply, Installation and Testing of 125mm deep Antivibration Flexible Joints made out of imported fire retardant fabric with extruded aluminium frame/ flange on both sides of approved make. | RM | 50 |  | 0
2.3 | Supply, Installation and Testing of multi blade type key operated louver dampers of galvanised steel sheet for collars to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | SqM | 6 |  | 0
2.4 | Supply, Installation and Testing of multiblade box type galvanised steel sheet dampers for ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | SqM | 3 |  | 0
2.5 | Supply, Installation and Testing of multiblade box type galvanised steel sheet dampers for elliptical ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sqm | 2 |  | 0
2.6 | Supply, Installation, Testing & Commissioning of Fire & Smoke dampers as per UL 555 and UL555S with at least 120 minutes fire rating as per the approved shop drawings and specifications. Fire damper shall be motorised spring return type with extended sleeve of 450mm. The dampers shall be of 16G sheet steel construction. The dampers shall be BMS compatible as per the specifications.
| a. Bare Fire & Smoke Dampers | SqM | 4 |  | 0
| b. Spring return type actuator with control panel, temperature sensor and suitable for 10 NM Torque. | No | 18 |  | 0
| c. Fusible Link Fire Dampers | Sqm | -- |  | Quote Rate
2.7 | Supply, Installation, Testing & Balancing of square supply air diffusers as per the approved shop drawings and specifications. Each diffuser shall be equipped with fixed air distribution grid, removable key-operated volume control damper. The diffusers shall be anti-smudge ring/ flush type.
Powder coated extruded aluminium diffusers of approved colour & shade of following sizes:
| a. 600x600 diffusers having neck size as mentioned in the "Approved for Construction" shop drawings suitable for fixing in Grid Ceiling. | No | 5 |  | 0
2.8 | Supply, Installation, Testing and Balancing of square diffusers same as supply air diffusers but without volume control dampers for return air as per the approved shop drawings and specifications.
Powder coated extruded aluminium diffusers of approved colour & shade of following sizes:
| a. 600x600 diffusers suitable for fixing in Grid Ceiling. | No | 5 |  | 0
2.9 | Supply, Installation, Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed inner core as per approved shop drawing and specifications. The grilles shall be of approved colour & shade.
a. Powder coated aluminium grille of extruded sections with integral flanges on both sides & ends as required.
| i. 100/150/200 mm High linear Grille | SqM | 6 |  | 0
| i. 100/150/200 mm High Curved Grille | SqM | 2 |  | 0
2.1 | Supply, Installation, Testing and Balancing of multi-slot type linear slot diffusers as per the approved shop drawings and specifications.
a. Powder coated extruded aluminium diffusers of approved colour & shade.
| i. 2/3/4 slot diffusers having width of slots as 25mm. | SqM | 8 |  | 0
2.11 | Supply, Installation, Testing and Commissioning of pre-insulated factory fabricated flexible ducts inner as well as outer skin constructed out of aluminium sheet. Ducts shall be of following sizes:
| a. 250mm dia | RM | -- |  | Quote Rate
| b. 200mm dia | RM | -- |  | Quote Rate
| c. 150mm dia | RM | 100 |  | 0
| d. 100mm dia | RM | -- |  | Quote Rate
2.12 | Supply, Installation & Testing of extruded aluminium powder coated air transfer grilles to be provided at toilets & kitchen doors. | SqM | 2 |  | 0
2.13 | Supply, Installation and Testing of multi-blade type non-return dampers of galvanised steel sheet construction with suitable links, levers and quadrants as per specifications and design drawings. | SqM | -- |  | Quote Rate
2.14 | Supply,Installation,Testing and commissioning of extruded aluminum powder coated fresh/exhaust air louver as per approved colour and shop drawings. The effective free area shall not be less than 70%. | SqM | -- |  | Quote Rate
2.15 | Supply, Installation and Testing of spigots of different sizes to facilitate flexible duct connection. Quoted price shall be inclusive of necessary clamping arrangement.
| a. 250mm dia | No | -- |  | Quote Rate
| b. 200mm dia | No | -- |  | Quote Rate
| c. 150mm dia | No | 140 |  | 0
| d. 100mm dia | No | -- |  | Quote Rate
TOTAL CARRIED TO SUMMARY (AIR DISTRIBUTION) Rs. |  |  |  |  | 0
3.0 | INSULATION
3.1 | Supply and Application of internal acoustic insulation of ducting using open cell elastomeric insulation with LEED compliant adhesive, longitudinal & transverse joints sealed with adhesive in neat & clean manner. All insulation joints shall have tape of same material with equivalent fire rating as the insulation.
| a. 25 mm thick | SqM | -- |  | Quote Rate
| b. 15 mm thick | SqM | 40 |  | 0
3.2 | Supply and Application of external thermal insulation of ducting using closed cell elastomeric insulation class O with glass cloth facing (EPDM) with LEED compliant adhesive, longitudinal & transverse joints sealed with adhesive to form proper bonding. All insulation joints shall have tape of same material with equivalent fire rating as the insulation. No additional remuneration shall be paid for flange insulation.
| a. 16 mm thick | SqM | 900 |  | 0
| b. 9 mm thick | SqM | -- |  | Quote Rate
3.3 | Supply and Application of 9 mm thick closed cell elastomeric insulation with glass cloth facing (EPDM) in tubing form for condensate drain piping as per the specifications.
Quoted price shall be inclusive of LEED Compliant adhesive and UV/ Mechanical Protection using resistant paint & Glass cloth/CSM as per specifications. All insulation joints shall have tape of same material with equivalent fire rating as the insulation.
| a. 40mm dia | RM | 250 |  | 0
| b. 32mm dia | RM | 310 |  | 0
| c. 25mm dia | RM | 350 |  | 0
3.4 | Supply and Application Closed cell elastomeric insulation for Roof exposed to sun using 25 mm thick closed cell elastomeric insulation with glass cloth facing (EPDM) material with factory faced glass cloth in sheet form with LEED compliant adhesive, longitudinal & transverse joints sealed with tape of same material as per specifications.
| a. 25 mm thick | SqM | -- |  | Quote Rate
TOTAL CARRIED TO SUMMARY (INSULATION) Rs. |  |  |  |  | 0
4 | ELECTRICAL INSTALLATION
4.1 | POWER CABLING
Supply, laying, affecting connections & Testing of the following sizes of 1.1 KV armoured XLPE insulated aluminium/ copper conductor cables. Cables shall be inclusive conductor cables. Cables shall be inclusive of all clamps, saddles, screws, cable identification tags, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required.
| a. 4C x 10 Sqmm cable (Copper) | RM | 120 |  | 0
| b. 4C x 6 Sqmm cable (Copper) | RM | 60 |  | 0
4.2 | CONTROL WIRING
Supply, laying, affecting connections and Testing of the following sizes of control cum transmission wiring to be laid in MS conduits between indoor units and outdoor units.
| 2C x1.5 Sqmm copper wiring | RM | 4500 |  | 0
4.3 | EARTHING
Providing & fixing in position the following bare GI tape/ GI or Cu wire including providing all fixing accessories & effecting proper connections.
| a. 8 SWG Cu Wire | RM | 350 |  | 0
TOTAL CARRIED TO SUMMARY (ELECTRICAL) Rs. |  |  |  |  | 0
Note:
GST shall be extra.

## HVAC LOW SIDE WORKS
PRICED SCHEDULE OF QUANTITIES
SUMMARY OF COSTS
ITEM | DESCRIPTION |  |  | AMOUNT (Rs.)
1. | EQUIPMENT |  |  | 0
2. | CONDENSER WATER PIPING |  |  | 0
3. | CHILLED |  |  | 0
4 | AIR DISTRIBUTION |  |  | 0
5. | INSULATION |  |  | 0
6. | ELECTRICAL |  |  | 0
TOTAL SUMMARY OF COSTS (INR) |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY. | RATE | AMOUNT | Venus Remarks/comments
1.0 | EQUIPMENT
1.1 | WATER COOLED SCREW CHILLERS
1.1.1 | Supply, Installation, Testing & Commissioning of AHRI certified water cooled chiller package of 180 TR actual capacity with unit mounted Air Cooled VFD with IP-55 protection (without AHF), comprising of helical rotary compressor/s with direct drive motor (the compressor speed shall not exceed 3000 RPM), insulated shell and tube type plain tube chiller as well as shell & tube type integrally finned condenser. The chiller package shall also be complete with vibration isolation mountings, copper refrigerant piping, full refrigerant charge, system control wiring and accessories as required. The chiller package shall be installed on a fabricated mild steel base frame assembled to form a compact assembly. The chiller package shall also be complete with microprocessor based control panel comprising of all adaptive controls, indication lights, VFD starter, over load and under load protection, TPN isolator for termination of incoming power cable, necessary control wiring, disconnect switch, mechanical couplings at in and out of both heat exchangers, DP switches for both heat exchangers & vibration isolation arrangement all complete as per the specifications.
The motor shall be suitable for operation on 415 ± 10% volts, 50 Hz, 3 Phase, AC power supply. The chiller package shall be BMS compatible. The water cooled screw chillers shall meet the following design parameters:
a. Chilled water leaving
temperature : 44 F (6.7 C)
b. Chilled water entering
temperature : 54 F (12.2 C)
c. Chiller fouling factor : 0.0005 sft.hr.F/BTU
d. Condenser water entering
temperature : 88 F (31.1 C)
e. Condenser water leaving
temperature : 98 F (36.6 C)
f. Condenser fouling factor : 0.001 sft.hr.F/BTU
g. Type of Refrigerant : R-134a
h. Certification : AHRI
i. Chiller and Condenser : 150 PSIG
Minimum Pressure Rating
j. Maximum permissible
IKW/TR at full load : 0.63
k. Minimum COP : 5.9
l. Minimum NPLV : 0.37
m. Minimum IPLV : 0.36
| Water cooled screw chillers as described above. | No | 2 |  | Owner | One more chiller will be install in future
1.1.2 | Clearance of chillers at nearest Port, Insurance Cover, Transportation to site at Chandigarh. Handling of chillers, lifting & shifting upto foundation on Terrace , positioning on foundation, Installation, Testing and Commissioning. | No | 2 |  | Owner
(Chilled water connections and cable termination at each chiller package shall be carried out by Low side vendor in co-ordination with the chiller manufacturer.)
Notes:
1.1.3 | Affecting chilled water, condenser water connections, cable termination and termination box etc. to make the installation complete by vendor in co-ordination with the chiller manufacturer. | No | 2 |  | 0
1.2.1 | CONDENSER WATER PUMPSETS
Supply, Installation, Testing and Commissioning of end suction type centrifugal pump sets factory assembled and tested for rated efficiency complete with IE-03 or above TEFC squirrel cage induction motor with class 'F' insulation, epoxy painted common base frame, flexible coupling, coupling guard, mechanical seals, vibration isolation arrangement etc. for recirculation of condenser water for the central air conditioning system as per the specifications. The pumps shall be suitable for operation on 415±10% Volts, 50 Hz, 3 Phase AC power supply. Quoted price shall be inclusive of inertia base with spring isolators for each pump. The pump characteristics shall be as follows:
Condenser water flow rate : 540 USGPM
(2041 LPM)
Head : 24 M
Maximum Permissible Speed : 1450 RPM
Motor Rating : 30 HP
| End suction pumps as described above including one standby. | No | 3 |  | 0
1.2.2 | CHILLED WATER PUMPSETS (PRIMARY) -- WCC
Supply, Installation, Testing and Commissioning of end suction type centrifugal pump sets factory assembled and tested for rated efficiency complete with IE-03, TEFC or above squirrel cage induction motor with class 'F' insulation, epoxy painted common base frame, flexible coupling, coupling guard, mechanical seals, vibration isolation arrangement etc. for recirculation of chilled water for the central air conditioning system as per the specifications. The pumps shall be suitable for operation on 415±10% Volts, 50 Hz, 3 Phase AC power supply. Quoted price shall be inclusive of inertia base with spring isolators for each pump. Pumps shall be insulated as per the specifications. The pump characteristics shall be as follows:
Chilled water flow rate : 432 USGPM
(1633 LPM)
Head : 12 M
Maximum Permissible Speed : 1450 RPM
Motor Rating : 10 HP
| End suction pumps as described above including one standby. | No | 3 |  | 0
1.2.3 | VARIABLE SPEED PUMPING SYSTEM
Supply, Installation, Testing and Commissioning of variable speed pumping system comprising of following accessories and as per the specifications. The system shall be complete in all respects including electrical components suitable for pump motor. Each pump shall have variable frequency drive. The entire system alongwith secondary CHW pumps shall be supplied through single vendor.
1.2.4.1 | For Chilled Water
a. | Variable frequency drive (VFD) : 3 Nos.
b. | Dedicated micro processor based pump controller : 1 No.
c. | Differential pressure sensors/ transmitters : 2 Nos.
d. | VSPS shall be BMS compatible and interfacing amongst all components and compatibility of I/O signals shall be provided : 1 Set
e. | Supply, Installation, Testing and Commissioning of end suction type centrifugal pump sets factory assembled and tested for rated efficiency complete with IE-02, TEFC squirrel cage induction motor with class 'F' insulation, epoxy painted common base frame, flexible coupling, coupling guard, mechanical seals, vibration isolation arrangement etc. for recirculation of chilled water for the central air conditioning system as per the specifications. The pumps shall be suitable for operation on 415±10% Volts, 50 Hz, 3 Phase AC power supply. Quoted price shall be inclusive of inertia base with spring isolators for each pump. Pumps shall be insulated as per the specifications. The pump characteristics shall be as follows:
Chilled water flow rate : 432 USGPM
(1633 LPM)
Head : 26 M
Maximum Permissible Speed : 1450 RPM
Motor Rating : 20 HP
End suction pumps as described above including one standby : 3 Nos.
Quoted price shall be inclusive of cabling and MS conduiting between pressure sensors and pump controller as per specifications.
| Variable Speed Pumping System as described above. | Set | 3 |  | 0
1.4 | COOLING TOWERS
Supply, Installation, Testing and Commissioning of FRP type induced draft single cell cooling towers with sump and steel ladder complete with, temperature sensor, IE-03 or Above TEFC squirrel cage high efficiency induction motor compatible with VFD, suitable for outdoor installation with necessary protection and uPVC fills as per the specifications. The cooling tower shall be suitable for 180 TR Screw Chillers. The cooling tower fan shall be suitable for operation on 415±10% Volts, 50 Hz, 3 Phase AC power supply. Heat rejection should be minimum 2700000 BTUs/Hr. Cooling Tower with duty conditions not restricted to the following:
a. Max. wet bulb temperature : 83 F (28.3 C)
b. Temperature of water entering cooling tower
: 98 F (36.6 C)
c. Temperature of water leaving cooling tower
: 88 F (31.1 C)
d. Water flow rate : 540 USGPM
(2040 LPM)
e. Max. fan speed : 960 RPM
f. Minimum efficiency of motors : 90%
| Induced draft single cell cooling towers as described above. | Nos. | 2 |  | 0 | One More Cooling tower may install in future
1.5 | AIR HANDLING UNITS (AHUs)
1.5.1 | HORIZONTAL FLOOR MOUNTED AIR HANDLING UNITS (HFM AHU) - WITH MIXING BOX (FOR CLEAN ROOMS)
Supply, Installation, Testing & Commissioning of Factory assembled/ modular Double Skin chilled water floor mounted type Air Handling Units (AHUs). AHUs shall be complete with double skin 50 mm thick insulated panels with CFC free polyurethane foam (PUF) insulation material with minimum density of 42 Kg/m3, sandwiched between 0.8 mm thick Aluminium Zinc Sheets (inner skin) and pre-coated G.I. Sheets (outer skin). The AHUs shall be complete with mixing box with necessary openings and aluminium dampers for teminating return air and fresh air ducts, and shall be provided with thermal break profile. Food grade self-adhesive coated EPDM gaskets shall be provided between panels and structure of the AHU to ensure the entire housing is airtight, and should meet clean room class leakage requirments as per Eurovent Standards. The AHUs shall be complete with 50mm thick pre-filter (MERV-8) section, 300 mm thick fine-filter (MERV-13) section, cooling coil section with multirows deep chilled water cooling coil of copper tube & aluminium fin construction to be sized for dehumidified CFM requirement & aluminium by-pass damper for remaining return air for achieving requisite air changes for Clean Rooms, EC Plug Fans, Ultrasonic Mist Generators with all controls & accessories, Re-heat section complete with finned type strip heaters, SS drain pan constructed from 18 gauge stainless steel & factory insulated with closed cell elastomeric Class 'O' material, copper header with "Copper to MS" adopter, all adaptive controls such as airstat, geyserstat, safetystat complete with wiring & vibration isolation pads etc. and all complete as per the specifications. AHUs shall be selected for a maximum face velocity of 500 FPM (2.5 MPS) and as per the Schedule of Air Handling Units. Fan outlet velocity shall not exceed 2000 FPM (10.2 MPS). AHUs should have marine lamps including adequately rated LED inside the AHU Cabinets. AHU inspection doors should have view windows with perfectly sealed gaksets on either side to ensure air tightness. All AHU doors shall be provided with door limit switch and door safety GI guard as well.
The AHUs shall be supplied with direct driven EC Plug Fan/s, complete with EC motor and buit-in controller. The EC Plug Fans shall be suitable for BMS soft integration with monitoring and control functions. The number of EC Plug Fans shall be selected with part-standby arrangement for redundancy. The AHUs shall be supplied with adequate cover plates for the EC Plug Fans from maintainance perspective. The AHUs shall be supplied with unit-mounted Electrical Panel complete with internal power cabling and control & communication wiring. All wiring and cabling within the unit and inside the electrical panel shall be executed at factory with approved makes of material. The Electrical Panel shall be equipped with Potentio-meter/s for manual fan speed control, auto/ manual selector switches and start stop push buttons for fans, phase-wise bank-wise MCBs as feeders for heater banks with NO/NC potential free contacts for BMS connectivity, and MCB/s as feeder for humdifier with NO/NC potential free contacts for BMS connectivity. All wire and cable terminations, looping etc. shall be carried out within the AHU and terminated at the utility interfaces of the Electrical Panel which shall be suitable for all EC Plug Fans' soft integration with BMS through RS-485 port/s, hard wired integration of heater banks and humidifier to BMS, and a single MCB/ MCCB for single incomming power cable termination for complete AHU with NO/NC contacts for AFAS Integration.
AHUs shall be of following design parameters:
HFM AHU Capacity SP No. of Coil Fans Fan Motor Rating Reheat
No. (Cfm) (mm WG) Rows (W+S/B) (kW) (kW)
| HFM AHU-1B 7300 120 6 2+1 3.7 (each) 20 | Nos. | 1 |  | 0 | Rate Only
| HFM AHU-2B 10000 120 6 2+1 3.7 (each) 29.5 | Nos. | 1 |  | 0
| HFM AHU-3B 7000 120 6 2+1 3.7 (each) 11 | Nos. | 1 |  | 0
| HFM AHU-4B 3500 120 6 1+1 3.7 (each) 6.5 | Nos. | 1 |  | 0
NOTE: Tender Design Basis shall be followed for determining on-coil and by-pass air requirement for each AHU.
1.5.2 | CEILING SUSPENDED AIR HANDLING UNITS (CS AHU) - WITH MIXING BOX
Supply, Installation, Testing & Commissioning of Factory assembled/ modular Double Skin chilled water ceiling suspended type Air Handling Units (AHUs). AHUs shall be complete with double skin 50 mm thick insulated panels with CFC free polyurethane foam (PUF) insulation material with minimum density of 42 Kg/m3, sandwiched between 0.8 mm thick pre-coated G.I. Sheets. The AHUs shall be complete with mixing box with necessary openings and aluminium dampers for teminating return air and fresh air ducts, and shall be provided with thermal break profile. Food grade self-adhesive coated EPDM gaskets shall be provided between panels and structure of the AHU to ensure the entire housing is airtight. The AHUs shall be complete with 50mm thick pre-filter (MERV-8) section, cooling coil section with multirows deep chilled water cooling coil of copper tube & aluminium fin construction, EC Plug Fan/s, SS drain pan constructed from 18 gauge stainless steel & factory insulated with closed cell elastomeric Class 'O' material, copper header with "Copper to MS" adopter, complete with wiring & vibration isolation pads etc. and all complete as per the specifications. AHUs shall be selected for a maximum face velocity of 500 FPM (2.5 MPS) and as per the Schedule of Air Handling Units. Fan outlet velocity shall not exceed 1800 FPM (9.1 MPS). Ceiling suspension arrangement for AHUs shall also include spring type vibration isolators/ rubber gromets etc. to make the installation vibration free.
The AHUs shall be supplied with direct driven EC Plug Fan/s, complete with EC motor and buit-in controller. The EC Plug Fans shall be suitable for BMS soft integration with monitoring and control functions. The AHUs shall be supplied with adequate cover plates for the EC Plug Fans from maintainance perspective. The AHUs shall be supplied with Electrical Panel complete with internal power cabling and control & communication wiring. All wiring and cabling within the unit and inside the electrical panel shall be executed at factory with approved makes of material. The Electrical Panel shall be equipped with Potentio-meter/s for manual fan speed control, auto/ manual selector switch/es and start stop push button/s for fan/s. All wire and cable terminations, looping etc. shall be carried out within the AHU and terminated at the utility interfaces of the Electrical Panel which shall be suitable for EC Plug Fan/s soft integration with BMS through RS-485 port/s, and a single MCB/ MCCB for single incomming power cable termination for complete AHU with NO/NC contacts for AFAS Integration.
AHUs shall be of following design parameters:
CS AHU Capacity SP No. of Coil Motor
No. (Cfm) (mm WG) Rows Rating (HP)
| CS AHU-1A 1200 40 6 1 x 1 | Nos. | 1 |  | 0
1.5.3 | CEILING SUSPENDED AHUs WITH EC FANS
Supply, Installation, Testing & Commissioning of Factory assembled/ modular Double Skin chilled water ceiling suspended/floor mounted type Air Handling Units (AHUs) complete with 50 mm insulation of CFC free polyurethane foam (PUF) panels of min 42 Kg/m3 density sandwiched between two layers of 0.8 mm thick perforated G.I. sheets. The control wiring and power wiring shall be in the scope of AHU manufactuer, and shall be carried out at factory with terminations to Marshalling Box.
The AHU shall be supplied with AHU blowers with wall mounted EC Plug Fan/s of EC motors approved makes of suitable ratings. The EC motors shall be suitable for BMS connectivity at one point. Single/ multiple fans shall be considered depending upon the capacity of the AHUs as mentioned below. AHU manufacturer should supply cover plate for Fans in sufficient quantities for maintanance purposes. EC Fans incoming supply shall be terminated with MCB/ MCCB and shall be included in the power terminal box for electrical connection of EC plug fans, and should be factory fitted on the AHUs. Potentio-meter shall be provided in the marshalling box for manual operation of EC fans. Relay for AUTO/MANUAL operation should be a part of Marshalling box supplied by the AHU manufacturer.
AHU control panel with display should be mounted on the AHU Body, and should have a single RS 485 output to the EC Fans integrated to BMS. AHU control panel should have NO/NC contacts for AFAS Integration. AHUs shall be suitable for BMS Integration and EC Fan speed modulatiion through DPS.
The air handling units shall be complete with Pre- filter (MERV-8), with the coil section with multi-rows deep chilled water cooling coil of copper tube and aluminium fin construction, insulated SS drain pan, copper header with "Copper to MS" adopter, and vibration isolation arrangement all complete as per the specifications. The AHUs shall be complete with mixing box with necessary openings and aluminium dampers for teminating return air and fresh air ducts, and shall be provided with thermal break profile.AHUs shall be selected for a maximum face velocity of 500 FPM (2.5 MPS) and fan outlet velocity shall not exceed 1800 FPM (9.1 MPS).
AHU should have marine lamp including adequately rated LED lamp inside the AHU Cabinet. AHU inspection door should have View Window with perfectly sealed gaksets on either side to ensure air tightness. All AHUs shall be provided with door limit switch and also door safety GI guard. All internals shall be powder coated for corrosion resistance.Quoted price shall be inclusive of hanging arrangments,associated elctrical works.
AHUs shall follow the design parameters as mentioned below:
AHU Capacity SP No. of Motor Area being fed
No. (Cfm) (mm WG) Rows Rating
(HP)
| AHU-1 2500 38 6 1x2 Conference Room | No | 1 |  | 0
| AHU-3 2500 38 6 1x2 UPS Room (North Block) | No | 1 |  | 0
| AHU-4 2500 38 6 1x2 UPS Room (South Block) | No | 1 |  | 0
| AHU-5,6 1800 38 6 1x1.5 Lobby | No | 2 |  | 0
| AHU-7,8 2500 38 6 1x2 Lobby | No | 2 |  | 0
| AHU-9 2500 38 6 1x2 UPS Room Audi | No | 1 |  | 0
| AHU-10 2000 38 6 1x2 IT Server Room | No | 1 |  | 0
| AHU-11,12 1500 38 6 1x1.5 Lobby | No | 2 |  | 0
| AHU-13,14 1500 38 6 1x1.5 Lobby | No | 2 |  | 0
| AHU-15,16 1500 38 6 1x1.5 Lobby | No | 2 |  | 0
| AHU-17,18 1500 38 6 1x1.5 Lobby | No | 2 |  | 0
| AHU-19 3500 38 6 1x3 Office & Archive Room | No | 1 |  | 0
| AHU-20,21 2500 38 6 1x2 Office & Archive Room | No | 2 |  | 0
| AHU-22,23 2500 38 6 1x2 Office & Archive Room | No | 2 |  | 0
| AHU-24 3500 38 6 1x3 Reception | No | 1 |  | 0
| AHU-25 2000 38 6 1x2 Pharmacology Lab | No | 1 |  | 0
| AHU-26 2000 38 6 1x2 Toxicology Lab | No | 1 |  | 0
| AHU-27 2500 38 6 1x2 Histopathology Lab & Microscope Area | No | 2 |  | 0
| AHU-28 1500 38 6 1x1.5 Sample Processing Drak Room | No | 1 |  | 0
| AHU-29 2000 38 6 1x2 Sample Processing Table | No | 1 |  | 0
| AHU-30 3500 38 6 1x3 Instrument Lab | No | 1 |  | 0
| AHU-31 3500 38 6 1x3 Molecular Lab | No | 1 |  | 0
| AHU-32 1500 38 6 1x1.5 Molecular Lab Store | No | 1 |  | 0
| AHU-33,34 1800 38 6 1x1.5 Office & Archive Room | No | 2 |  | 0
| AHU-35,36 3000 38 6 1x3 Office & Archive Room | No | 2 |  | 0
| AHU-37,38 3000 38 6 1x3 Office & Archive Room | No | 2 |  | 0
| AHU-39,40 3000 38 6 1x3 Office & Archive Room | No | 2 |  | 0
| AHU-41,42 3000 38 6 1x3 Office & Archive Room | No | 2 |  | 0
| AHU-43,44 3000 38 6 1x3 Office & Archive Room | No | 2 |  | 0
| AHU-45 3000 38 6 1x3 Office & Archive Room | No | 1 |  | 0
| AHU-46 1500 38 6 1x1.5 Admin Office | No | 1 |  | 0
| AHU-47 2000 38 6 1x2 Kitchen | No | 1 |  | 0
| AHU-48 1200 38 6 1x1.5 Reception | No | 1 |  | 0
| AHU-49 2000 38 6 1x2 UPS & Battery Room | No | 1 |  | 0
| AHU-50 4500 38 6 1x3 Annap. Dinning Hall, Store & Pre-Serving | No | 1 |  | 0
| AHU-51 3500 38 6 1x3 Annapurna Dinning Hall RHS | No | 1 |  | 0
1.5.4 | AIR HANDLING UNITS WITH EC FANS
Supply, Installation, Testing & Commissioning of Factory assembled/ modular Double Skin chilled water ceiling suspended/floor mounted type Air Handling Units (AHUs) complete with 50 mm insulation of CFC free polyurethane foam (PUF) panels of min 42 Kg/m3 density sandwiched between two layers of 0.8 mm thick perforated G.I. sheets. The control wiring and power wiring shall be in the scope of AHU manufactuer, and shall be carried out at factory with terminations to Marshalling Box.
The AHU shall be supplied with AHU blowers with wall mounted EC Plug Fan/s of EC motors approved makes of suitable ratings. The EC motors shall be suitable for BMS connectivity at one point. Single/ multiple fans shall be considered depending upon the capacity of the AHUs as mentioned below. AHU manufacturer should supply cover plate for Fans in sufficient quantities for maintanance purposes. EC Fans incoming supply shall be terminated with MCB/ MCCB and shall be included in the power terminal box for electrical connection of EC plug fans, and should be factory fitted on the AHUs. Potentio-meter shall be provided in the marshalling box for manual operation of EC fans. Relay for AUTO/MANUAL operation should be a part of Marshalling box supplied by the AHU manufacturer.
AHU control panel with display should be mounted on the AHU Body, and should have a single RS 485 output to the EC Fans integrated to BMS. AHU control panel should have NO/NC contacts for AFAS Integration. AHUs shall be suitable for BMS Integration and EC Fan speed modulatiion through DPS.
The air handling units shall be complete with The AHUs shall be complete with 50mm thick pre-filter (MERV-8), Fine filter (MERV-14), section, with the coil section with multi-rows deep chilled water cooling coil of copper tube and aluminium fin construction, insulated SS drain pan, copper header with "Copper to MS" adopter, and vibration isolation arrangement all complete as per the specifications.. The AHUs shall be complete with mixing box with necessary openings and aluminium dampers for teminating return air and fresh air ducts, and shall be provided with thermal break profile AHUs shall be selected for a maximum face velocity of 500 FPM (2.5 MPS) and fan outlet velocity shall not exceed 1800 FPM (9.1 MPS).
AHU should have marine lamp including adequately rated LED lamp inside the AHU Cabinet. AHU inspection door should have View Window with perfectly sealed gaksets on either side to ensure air tightness. All AHUs shall be provided with door limit switch and also door safety GI guard. All internals shall be powder coated for corrosion resistance.Quoted price shall be inclusive of foundations,associated elctrical works.
AHUs shall follow the design parameters as mentioned below:
AHU Capacity SP No. of Motor Area being fed
No. (Cfm) (mm WG) Rows Rating
(HP)
| AHU-2 17000 60 6 1x10 Auditorium | No | 1 |  | 0
1.6 | TREATED FRESH AIR UNITS (TFAUs)
1.6.1 | TREATED FRESH AIR UNITS WITH EC FANS -- TFAUs
Supply, Installation, Testing & Commissioning of Factory assembled/ modular Double Skin chilled water floor mounted type Treated Fresh Air Units (TFAs) complete with 50 mm insulation of CFC free polyurethane foam (PUF) panels of min 42 Kg/m3 density sandwiched between two layers of 0.8 mm thick perforated G.I. sheets. The control wiring and power wiring shall be in the scope of TFA manufactuer, and shall be carried out at factory with terminations to Marshalling Box.
The TFA shall be supplied with TFA blowers with wall mounted EC Plug Fan/s of EC motors approved makes of suitable ratings. The EC motors shall be suitable for BMS connectivity at one point. Single/ multiple fans shall be considered depending upon the capacity of the TFAs as mentioned below. TFA manufacturer should supply cover plate for Fans in sufficient quantities for maintanance purposes. EC Fans incoming supply shall be terminated with MCB/ MCCB and shall be included in the power terminal box for electrical connection of EC plug fans, and should be factory fitted on the TFAs. Potentio-meter shall be provided in the marshalling box for manual operation of EC fans. Relay for AUTO/MANUAL operation should be a part of Marshalling box supplied by the TFA manufacturer.
TFA control panel with display should be mounted on the TFA Body, and should have a single RS 485 output to the EC Fans integrated to BMS. TFA control panel should have NO/NC contacts for AFAS Integration. TFAs shall be suitable for BMS Integration and EC Fan speed modulatiion through DPS.
The Treated Fresh air units shall be complete with Pre- filter (MERV-8), fine filter (MERV-13) ,with the coil section with multi-rows deep chilled water cooling coil of copper tube and aluminium fin construction, insulated SS drain pan, copper header with "Copper to MS" adopter, and vibration isolation arrangement all complete as per the specifications. The TFAs shall be complete with mixing box with necessary openings and aluminium dampers for teminating fresh air ducts, and shall be provided with thermal break profile.TFAs shall be selected for a maximum face velocity of 500 FPM (2.5 MPS) and fan outlet velocity shall not exceed 1800 FPM (9.1 MPS).
TFA should have marine lamp including adequately rated LED lamp inside the TFA Cabinet. TFA inspection door should have View Window with perfectly sealed gaksets on either side to ensure air tightness. All TFAs shall be provided with door limit switch and also door safety GI guard. All internals shall be powder coated for corrosion resistance.Quoted price shall be inclusive of hanging arrangments,associated elctrical works.
TFAs shall follow the design parameters as mentioned below:
TFA Capacity SP No. of Motor
No. (Cfm) (mm WG) Rows Rating (HP)
| TFA-1 11700 55 6 7.5 | No | 1 |  | 0
| TFA-2 5100 55 6 5 | No | 1 |  | 0
| TFA-3 8000 55 6 5 | No | 1 |  | 0
1.6.2 | TREATED FRESH AIR UNITS -- TFAUs
(CEILING SUSPENDED)
Supply, Installation, Testing & Commissioning of Factory assembled/ modular Double Skin chilled water ceiling suspended/floor mounted type Treated Fresh Air Units (TFAs) complete with 50 mm insulation of CFC free polyurethane foam (PUF) panels of min 42 Kg/m3 density sandwiched between two layers of 0.8 mm thick perforated G.I. sheets. The control wiring and power wiring shall be in the scope of TFA manufactuer, and shall be carried out at factory with terminations to Marshalling Box.
The TFA shall be supplied with TFA blowers with wall mounted EC Plug Fan/s of EC motors approved makes of suitable ratings. The EC motors shall be suitable for BMS connectivity at one point. Single/ multiple fans shall be considered depending upon the capacity of the TFAs as mentioned below. TFA manufacturer should supply cover plate for Fans in sufficient quantities for maintanance purposes. EC Fans incoming supply shall be terminated with MCB/ MCCB and shall be included in the power terminal box for electrical connection of EC plug fans, and should be factory fitted on the TFAs. Potentio-meter shall be provided in the marshalling box for manual operation of EC fans. Relay for AUTO/MANUAL operation should be a part of Marshalling box supplied by the TFA manufacturer.
TFA control panel with display should be mounted on the TFA Body, and should have a single RS 485 output to the EC Fans integrated to BMS. TFA control panel should have NO/NC contacts for AFAS Integration. TFAs shall be suitable for BMS Integration and EC Fan speed modulatiion through DPS.
The Treated Fresh air units shall be complete with Pre- filter (MERV-8), with the coil section with multi-rows deep chilled water cooling coil of copper tube and aluminium fin construction, insulated SS drain pan, copper header with "Copper to MS" adopter, and vibration isolation arrangement all complete as per the specifications. The TFAs shall be complete with mixing box with necessary openings and aluminium dampers for teminating fresh air ducts, and shall be provided with thermal break profile.TFAs shall be selected for a maximum face velocity of 500 FPM (2.5 MPS) and fan outlet velocity shall not exceed 1800 FPM (9.1 MPS).
TFA should have marine lamp including adequately rated LED lamp inside the TFA Cabinet. TFA inspection door should have View Window with perfectly sealed gaksets on either side to ensure air tightness. All TFAs shall be provided with door limit switch and also door safety GI guard. All internals shall be powder coated for corrosion resistance.Quoted price shall be inclusive of hanging arrangments,associated elctrical works.
TFAs shall follow the design parameters as mentioned below:
TFA Capacity SP No. of Motor
No. (Cfm) (mm WG) Rows Rating (HP)
| TFA-5,6 700 38 6 1 | No | 2 |  | 0
| TFA-7 900 38 6 1 | No | 1 |  | 0
| TFA-8 1900 38 6 2 | No | 1 |  | 0
| TFA-9 400 38 6 1 | No | 1 |  | 0
| TFA-10 1200 38 6 1.5 | No | 1 |  | 0
1.6.3 | TREATED FRESH AIR UNITS -- TFAUs
(WITH FACE & BYPASS ARRANGEMENT)
Supply, Installation, Testing & Commissioning of double skin sheet metal sectionalised construction treated fresh air units , double skin panels with 46mm thick injected PUF of density not less than 40Kg/CuM with thermal break profile. The treated fresh air units shall be complete with pre-filter (MERV-8), fine filter (MERV-13), face & bypass damper, multi rows deep chilled water cooling coil of copper tube and aluminium fins, backward curved DIDW centrifugal fan, belt drive package, insulated SS drain pan, copper header, "Copper to MS" adopter, IE-03 or Above squirrel cage induction motor and vibration isolation arrangement all complete as per specifications. TFAs shall be selected for a maximum face velocity of 500 FPM (2.5MPS) and as per schedule of air handling units under Appendix VIII. Fan outlet velocity shall not exceed 1800 FPM (9.1MPS) for ceiling suspended & 2000 FPM (10.1 MPS) for floor mounted TFAUs. The unit/s shall be be provided with factory fabricated plenum on filter side, with access doors /panels, for duct termination. TFAUs shall be of following design parameters:
F&B TFA-4 (KITCHEN)
Air Quantity Face - 5100 Cfm
Air Quantity Bypass - 3400 Cfm
Total Air Quantity - 8500 Cfm
Static Pressure - 55 mm WG
CHW Coils - 6 Rows
Motor Rating - 5 HP
| Type - FM | No | 1 |  | 0
1.7 | CHILLED BASED CASSETTE/ HI-WALL UNITS
Supply, Installation, Testing and Commissioning of chilled water based cassette type indoor units suitable for two pipe system. These units shall consist of a fan section with dynamically balanced centrifugal fan/s driven by FHP/TEFC squirrel cage induction motor, multirows deep separate cooling coil & heating coil of copper tubes and aluminium fins etc. Enclosures shall be fabricated as specified for Dx split units. These units shall be equipped with synthetic fibre filters, insulated drain pan, safety controls, thermostat, a set of valve station with pair of ball valves (one with strainer and one without strainer) and self balancing pressure independent flow control valves etc. all complete in a unit. The unit shall be provided with BMS compatible Kit. The quoted price shall be inclusive of vibration isolation arragement for ceiling suspension, associated electrical work, drain pump for condensate removal etc.
| a. 1.5 TR nominal capacity Cassette type unit (chilled water based) with cordless control. | No | 2 |  | 0
| b. 1.0 TR nominal capacity Cassette type unit (chilled water based) with cordless control. | No | 4 |  | 0
| c. 1.5 TR nominal capacity Hi wall unit (chilled water based) with cordless control. | No | 2 |  | 0
| d. 1.0 TR nominal capacity Hi wall unit (chilled water based) with cordless control. | No | 6 |  | 0
| e. 0.75 TR nominal capacity Hi wall unit (chilled water based) with cordless control. | No | 3 |  | 0
1.8 | FAN COIL UNITS
Supply of fan coil units each comprising of 3 rows deep chilled water cooling coil, centrifugal blowers, FHP motor, metallic cleanable filters, insulated & extended condensate drain pan, casing, coil piping connections, condensate drain piping connections & wiring. Fan coil units shall be suitable for operation on 220 + 6% Volts, 50Hz, single phase power supply of following sizes & capacities.
Ceiling Concealed Fan Coil Units:
| i. 2.5 TR nominal capacity with 900-1000 Cfm air quantity. | No | 4 |  | 0
| ii. 2.0 TR nominal capacity with 800-900 Cfm air quantity. | No | 6 |  | 0
| iii. 1.5 TR nominal capacity with 600-700 Cfm air quantity. | No | 9 |  | 0
| iv. 1.0 TR nominal capacity with 400-500 Cfm air quantity. | No | 31 |  | 0
| v. 0.75 TR nominal capacity with 300-350 Cfm air quantity. | No | 11 |  | 0
1.9 | EXTRACT FAN SECTIONS
1.9.1 | FOR KITCHENS
Supply, Installation, Testing and Commissioning of approved make fan section for extract air complete with floor standing backward curved DIDW centrifugal fan, MS base frame, IE-03 TEFC squirrel cage induction motor with 2 hour fire rating & class "H" insulation, drive package and vibration isolation arrangement including spring isolators, rubber grommets etc. as called for in working drawings & specifications. Fan section casing shall be of double skin sheet metal construction, double skin panels with 25mm thick injected PUF of density not less than 40 kg/CuM. Fan shall be suitable for operation on 415 ± 10% volts, 50 Hz 3 phase AC power supply. Fan motor for kitchen fan, shall be enclosed in GI sheet enclosure enclosure in hot air stream free area. Fan outlet velocity shall not exceed 2000 FPM. Extract fan section shall be suitable for ceiling suspension/floor installation as shown in the design drawings.The kitchen fan motor shall be outside hot air stream. The fan characteristics shall be as follows:
Fan Capacity S.P Motor Type
No. (Cfm) (mmWG) Rating
(HP)
| EFS-1 10000 65 7.5 FM | No | 1 |  | 0
1.9.2 | FOR TOILETS, PANTRIES DISH WASH ETC.
Supply, Installation, Testing and Commissioning of approved make fan section for extract air complete with forward curved DIDW centrifugal fan, MS base frame, IE-03 TEFC squirrel cage induction motor with class "F" insulation, drive package and vibration isolation arrangement including spring isolators, rubber grommets etc. as called for in working drawings & specifications. Fan section casing shall be of double skin sheet metal construction, double skin panels with 25mm thick injected PUF of density not less than 40 kg/CuM. Fan shall be suitable for operation on 415 ± 10% volts, 50 Hz 3 phase AC power supply. Fan outlet velocity shall not exceed 2000 FPM for FM Units & 1800 FPM for CS Units. Extract fan section shall be suitable for ceiling suspension/floor installation as shown in the design drawings. The fan characteristics shall be as follows:
Fan Capacity S.P Motor Type
No. (Cfm) (mmWG) Rating
(HP)
| EFS- 1400 30 1 CS | No | -- |  | Quote Rate
1.9.3 | EXHAUST AIR SCRUBBER
Supply, Installation, Testing and Commissioning of Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove odour, smoke and fumes from exhaust air. Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14" deep cell, to work as magnet for charged smoke and oil particles.
Average efficiency of 90-95% in single pass as per DOP test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air cleaner.
Operating Voltage : 220V, 50 Hz
Ionizing Voltage : 12.5 to 13 KVDC
Collector Cell Voltage : 6 to 6.5 KVDC
Power Consumption : 50 Watts
| 5000 CFM x 2 filters | No | 1 |  | 0
1.1 | INLINE FANS
Supply, Installation, Testing and Commissioning of circular/rectangular inline fans for exhaust air as shown on drawings, complete with sheet metal casing, direct driven centrifugal fan, motor with proper protection and inspection door,gravity louvers etc. as per the specifications. Fan should be suitable for operation on 415+10% volts, 50 Hz, three phase or 220±10 %, 50 Hz, single phase AC power supply as required. Single Phase inline fans shall be provided with speed regulators.
Fan shall be suitable for installation or as shown on drawings and shall be of following capacities:
Fan Capacity SP Electrical Type
No. (Cfm) (mmWG) Characteristics
| IF- 900 15 220V/1 Ph Circular | No | -- |  | Quote Rate
| IF- 800 15 220V/1 Ph Circular | No | -- |  | Quote Rate
| IF- 700 15 220V/1 Ph Circular | No | 11 |  | 0
| IF- 600 15 220V/1 Ph Circular | No | -- |  | Quote Rate
| IF- 500 15 220V/1 Ph Circular | No | 4 |  | 0
| IF- 400 12 220V/1 Ph Circular | No | 11 |  | 0
| IF- 300 12 220V/1 Ph Circular | No | 3 |  | 0
| IF- 200 12 220V/1 Ph Circular | No | 9 |  | 0
| IF- 150 12 220V/1 Ph Circular | No | 3 |  | 0
| IF- 100 12 220V/1 Ph Circular | No | 8 |  | 0
1.11 | AXIAL FLOW FANS
AXIAL FLOW FANS FOR EXHAUST (AF)
1.11.1 | Emergency Exhaust:
Supply, Installation, Testing & Commissioning of AMCA Certified (For Air and Sound Performance) tube axial flow fans of different capacities in standard GI/M.S. construction as mentioned below. Entire fan model and AMCA Seal shall appear in technical submittal of fan. All the fans shall be either galvanized steel with a coating of Z275 or mild steel that is hot dipped galvanized to DIN EN ISO 1461and complete with bird screen at fan inlet/outlet. The electric motor coupler shall be IE-03 squirrel cage induction type conforming to IS-325, IP-55 rated with class `H' insulation. Motor shall be of high temperature resistance "Class H Smoke Spill" 250°C for 2 hours. Fans shall be EN 12101-3 Certified and CE/UL Listed for high temperature. Motor make shall be same as that mentioned on the fire certificate. Fan efficiency should not be less than 70%, and noise level should not be more than 85 db @ 3 m distance when measured under hemispherical reverberant room conditions. Quoted price shall be inclusive of sound attenuator at the outlet /inlet of the fan to achieve desired sound levels of the fan as shown in the approved shop drawings, all accessories like bird screens, vibration isolators, mounting brackets/feet/ duly enamel painted M.S structure etc. Fans mentioned as outdoor type shall be good for outdoor installation with proper cowl and mounting arrangement as per approved shop drawings. Fans shall be as per specifications and design drawings. Axial Flow Fans shall follow the design parameters as mentioned below:
AF Capacity SP Motor Type Area Being Fed
No. (Cfm) (mm WG) Rating
(HP)
Smoke Ventilation
| AF-1 5300 25 3 Indoor Lounge / Waiting Area & Corridor | No | 1 |  | 0
| AF-5,4,5&6 7800 25 5 Indoor Open Office Space /Corridor & Reception | No | 4 |  | 0
| AF-11 4900 25 3 Indoor Open Office Space /Corridor & Reception | No | 1 |  | 0
| AF-13 4800 25 3 Indoor Open Office Space /Corridor & Reception | No | 1 |  | 0
| AF-15 2000 25 1.5 Indoor Annapurna Dinning Hall | No | 1 |  | 0
| AF-17 2000 25 1.5 Indoor Annapurna Dinning Hall RHS | No | 1 |  | 0
| AF-19 1600 25 1.5 Indoor Director/Dawat Dining Hall | No | 1 |  | 0
| AF-21,22 19600 25 10 Indoor Audi | No | 2 |  | 0
| AF-25 3500 25 2 Indoor Open Office Space /Corridor & Reception | No | 1 |  | 0
| AF-27 6500 25 3 Indoor Open Office Space /Corridor & Reception | No | 1 |  | 0
| AF-29 6700 25 3 Indoor Open Office Space /Corridor & Reception | No | 1 |  | 0
AXIAL FLOW FANS FOR FRESH AIR SUPPLY (AF)
1.11.2 | Emergency Supply:
Supply, Installation, Testing & Commissioning of AMCA Certified (For Air and Sound Performance) tube axial flow fans of different capacities in standard GI/M.S. construction as mentioned below. Entire fan model and AMCA Seal shall appear in technical submittal of fan. All the fans shall be either galvanized steel with a coating of Z275 or mild steel that is hot dipped galvanized to DIN EN ISO 1461and complete with bird screen at fan inlet/outlet. The electric motor coupler shall be IE-03 squirrel cage induction type conforming to IS-325, IP-55 rated with class `F' insulation. Fan efficiency should not be less than 70%, and noise level should not be more than 85 db @ 3 m distance when measured under hemispherical reverberant room conditions. Quoted price shall be inclusive of sound attenuator at the outlet /inlet of the fan to achieve desired sound levels of the fan as shown in the approved shop drawings, all accessories like bird screens, vibration isolators, mounting brackets/feet/ duly enamel painted M.S structure etc. Fans mentioned as outdoor type shall be good for outdoor installation with proper cowl and mounting arrangement as per approved shop drawings. Fans shall be as per specifications and design drawings. Fans shall be as per specifications and design drawings. Axial Flow Fans shall follow the design parameters as mentioned below:
AF Capacity SP Motor Type Area Being Fed
No. (Cfm) (mm WG) Rating
(HP)
Smoke Ventilation
| AF-2 5300 25 3 Indoor Lounge / Waiting Area & Corridor | No | 1 |  | 0
| AF-7,8,9&10 7800 25 5 Indoor Open Office Space /Corridor & Reception | No | 4 |  | 0
| AF-12 4900 25 3 Indoor Open Office Space /Corridor & Reception | No | 1 |  | 0
| AF-14 4800 25 3 Indoor Open Office Space /Corridor & Reception | No | 1 |  | 0
| AF-16 2000 25 1.5 Indoor Annapurna Dinning Hall | No | 1 |  | 0
| AF-18 2000 25 1.5 Indoor Annapurna Dinning Hall RHS | No | 1 |  | 0
| AF-20 1600 25 1.5 Indoor Director/Dawat Dining Hall | No | 1 |  | 0
| AF-23,24 19600 25 10 Indoor Audi | No | 2 |  | 0
| AF-26 3500 25 2 Indoor Open Office Space /Corridor & Reception | No | 1 |  | 0
| AF-28 6500 25 3 Indoor Open Office Space /Corridor & Reception | No | 1 |  | 0
| AF-30 6700 25 5 Indoor Open Office Space /Corridor & Reception | No | 1 |  | 0
PRESSURIZATION
LIFT WELL
| AF- 7500 25 5 Outdoor Lift Well-1,2,3&4 | No | 4 |  | 0
31,32,33&34
| AF-35,36 7000 25 5 Outdoor Lift Well-1A & 2A | No | 2 |  | 0
| AF-37 7000 25 5 Outdoor Service Lift Well | No | 1 |  | 0
| AF-38 7000 25 5 Outdoor Service Lift Well (North Block) | No | 1 |  | 0
1.12 | VARIABLE FREQUENCY DRIVES
Supply, Installation, Testing & Commissioning of variable frequency drives for following Air Handling Units/ Axial Flow Fans, Extract fan Sections. Variable frequency drives shall be provided with necessary temperature sensors and controllers complete with control wiring in all respect as required and as per the specifications. The drives shall be suitable for the following motor rating. VFDs shall be housed in AHU/ FAN panels.
| i. 12.5 HP | No | -- |  | Quote Rate
| ii. 10 HP | No | -- |  | Quote Rate
1.13 | AIR & SURFACE DISINFECTING OH RADICAL GENERATORS - DUCT MOUNTED (COMMON AREAS)
Supply, Installation, Testing and commissioning of duct mounted Hydroxyl Radical Generators for Air & Surface disinfection for use within occupied building spaces. The device shall be compatible with 220 V + 10%, 50 Hz, Single Phase AC Power Supply. The unit shall be capable of producing human friendly Hydroxyl Radicals and Organic Oxidants and cater upto 3000 Square Feet of Area fed by a single supply air duct. OEM shall produce 13 week GLP toxicology report on the technology used in the device to support human safety claims. The unit shall be capable of reducing indoor air pollutants such as Viruses, Bacteria, Fungus, VOCs, and odors - the OEM must produce lab test reports from reputed international laboratories against at least 10 different types of pathogens. The OEM must also produce COVID-19 causing Coronavirus Reduction Test Reports from reputed International BSL3 Laboratory, with minimum reduction in virus load of 99% in 20 minutes or less in air, and in 60 mins or less on surfaces. The technology used in the device should have USFDA approval, and should have recommendation for use from DRDO/ ICMR in India for COVID-19. The quoted price shall be inclusive of power to be drawn to Hydroxyl Radical Generators from the respective AHU Starter Panels including but not limited to the following - power/ control cabling, MS conduiting, 6A DP MCB isolator, socket near the unit etc. so that these units only operate when the AHUs are in operation. Certifications shall be submitted along with the technical submitals, refer technical specififcations for required compliances. The Hydroxyl Radical Generators shall be suitable for the following area of treatment:
| i. Upto 3000 Sqft | Nos | 60 |  | 0
NOTE: Selections shall be shared based on OEM Standards.
1.14 | COMMISSIONING FILTERS (MERV-8)
| Supply, Installation, Testing and Commissioning of Pre-filters (MERV- 8) Filters for Air Handling Units. Building Flush out shall be carried out during construction stage and post construction stage with required fans. It shall be conducted as per LEED and Clean Room guidelines. | SqM | 40 |  | 0
1.15 | Supply, Installation, Testing and Balancing of following sizes Terminal Mini Pleat Gel Seal HEPA Filter Box Type, Grade: H14, consisting of Terminal HEPA Module, Top Air Inlet, Flange Type with Filter Loading from Bottom (Clean Room side), Glass Fiber Filter Media with Hot Melt Separator, MOC of Filter Frame shall be - Aluminum Anodized Extrusion, MOC of Housing shall be - 13G Aluminum Powder Coated Extrusion, Pressure measurement ports, PAO concentration Port, Al. Aerofoil Volume Control Sqaure Type Damper with worm gear (operated from room side), Diffuser Plate with 18G SS Perforation Sheet at Bottom (Capsule Design 60% Opening). Housing Loading shall be from Bottom (Clean Room side). Average Filtration Efficiency shall be 99.999% down to 0.3 μm, with bothside Face Guard, and each filter shall be Auto Scan Tested in accordance with EN1822 standard and manufactured in Class 100000 Clean Room. HEPA filters shall be installed as per the approved shop drawings and specifications, and shall be of following sizes:
| a. 600mmx600mmx150mm (Thick) | No | 22 |  | 0
| b. 600mmx600mmx300mm (Thick) | No | -- |  | Quote Rate
1.16 | Magnehelic Gauge
| Scope includes the supply, installation, testing, and commissioning of a Magnehelic gauge with a pressure measurement range of 0–50 Pa, complete with calibration nozzles and high-quality PVC tubing. The tubing shall be installed to facilitate pressure readings across the designated room, ensuring accurate differential pressure monitoring. The entire setup shall be carried out in accordance with relevant standards and shall be suitable for cleanroom or HVAC applications, as applicable | Nos | 8 |  | 0
TOTAL CARRIED TO SUMMARY (EQUIPMENT) Rs. |  |  |  |  | 0
2.0 | CONDENSER WATER PIPING
2.1 | Providing and fixing in position the following MS heavy class pipes cut to required lengths and installed with all welded joints. Providing and fixing in position the necessary fittings like elbows, tees, reducers, hanging arrangement including vibration isolation arrangements with anti-seismic feature etc. as required.
| a. 300mm dia (8mm thick) | RM | -- |  | Quote Rate
| b. 250mm dia (6mm thick) | RM | 140 |  | 0
| c. 200mm dia (6mm thick) | RM | 10 |  | 0
| d. 150mm dia | RM | 100 |  | 0
| e. 125mm dia | RM | 10 |  | 0
| f. 100mm dia | RM | 60 |  | 0
2.2 | Providing and fixing in position the following wafer type Butterfly Valves complete with companion flanges, nuts, bolts, gaskets etc. as required. Butterfly valves shall conform to PN-16 rating as per specifications.
| a. 250mm dia | No | -- |  | Quote Rate
| b. 150mm dia | No | 9 |  | 0
| c. 100mm dia | No | 3 |  | 0
2.3 | Providing and fixing in position the following Motorised Butterfly Valves with all accessories as required. Butterfly valves shall conform to PN-16 rating as per specifications.The valve shall be BMS compatible.
| a. 250mm dia | No | -- |  | Quote Rate
| b. 150mm dia | No | 9 |  | 0
2.4 | Providing and fixing in position the following Ball Valves as per the specifications.
| a. 40mm dia | No | 5 |  | 0
| b. 32mm dia | No | 5 |  | 0
2.5 | Providing and fixing in position the following specified make balancing valves. Balancing valves shall conform to PN -16 rating as per the specifications.
| a. 250mm dia | No | -- |  | Quote Rate
| b. 150mm dia | No | 6 |  | 0
2.6 | Providing and fixing in position the following wafer type dual plate check valves. Check valves shall conform to PN-16 rating as per the specifications.
| a. 250 mm dia | No | -- |  | Quote Rate
| b. 150 mm dia | No | 3 |  | 0
2.7 | Providing and fixing in position the following automatic purge valves. Purge valves shall conform to PN-16 rating. | No | 6 |  | 0
2.8 | Providing and fixing in position industrial type pressure gauges constructed out of SS 304 material. SS siphon shall be factory insulated with closed cell elastomeric insulation in tubing form. Pressure gauges shall be factory fitted with a ball valve at the tube. | No | 12 |  | 0
2.9 | Supply and fixing in position V-form industrial type thermometers as per the specifications. | No | 6 |  | 0
2.10 | Providing and fixing in position the following suction guides with strainer for condenser water pumps. The suction guides shall be installed at the inlet of each pump and rated for 16 Bar (PN-16) operating pressure. Suction guide shall have SG Iron/ MS body with wall thickness minimum 8mm. Suction guide shall be complete with outlet guide vanes, removable SS strainers and fine mesh SS start-up strainer. The connecting flanges shall be raised face type. Each suction guide shall be provided with 1/2" dia. ball type blow down valve.
| a. 250mm dia | No | -- |  | Quote Rate
| b. 150mm dia | No | 3 |  | 0
2.11 | Supply & Installation of neoprene rubber expansion belows with integral reinforced rubber flanges, guide rods on both sides at inlet & outlet of water chilling machines and condenser water pumps of approved make.
| a. 250mm dia | No | -- |  | Quote Rate
| b. 150mm dia | No | 12 |  | 0
2.12 | Providing and fixing in position approved make differential pressure switches complete with copper control wiring at condenser water outlet of each machine. | Sets | 3 |  | 0
2.13 | Supply & application of 1.5mm thick FRP lining on condenser water piping within cooling tower yard on terrace.
| a. 300mm dia (6mm thick) | RM | -- |  | Quote Rate
| b. 250mm dia (6mm thick) | RM | 100 |  | 0
| c. 200mm dia (6mm thick) | RM | -- |  | Quote Rate
| d. 150mm dia | RM | 70 |  | 0
| e. 125mm dia | RM | 10 |  | 0
| f. 100mm dia | RM | 60 |  | 0
2.14 | Providing and fixing in position the following GI medium class pipes for drain cut to required lengths & installed with all screwed joints and providing & fixing in position the necessary elbows, tees & reducers.
| a. 40mm dia | RM | 25 |  | 0
| b. 32mm dia | RM | 30 |  | 0
TOTAL CARRIED TO SUMMARY (CDW PIPING) Rs. |  |  |  |  | 0
3.0 | CHILLED WATER PIPING
3.1 | Providing and fixing in position the following MS heavy class pipes cut to required lengths and installed with all welded joints. Providing & fixing in position the necessary fittings like elbows, tees, reducers, hanging arrangement including vibration isolation arrangements with anti-seismic feature etc. as required.
| a. 250mm dia (6mm thick) | RM | -- |  | Quote Rate
| b. 200mm dia (6mm thick) | RM | 180 |  | 0
| c. 150mm dia | RM | 120 |  | 0
| d. 125mm dia | RM | 100 |  | 0
| e. 100mm dia | RM | 110 |  | 0
| f. 80mm dia | RM | 90 |  | 0
| g. 65mm dia | RM | 80 |  | 0
| h. 50mm dia | RM | 100 |  | 0
| i. 40mm dia | RM | 210 |  | 0
| j. 32mm dia | RM | 350 |  | 0
| k. 25mm dia | RM | 250 |  | 0
| l. 20mm dia | RM | 450 |  | 0
3.2 | Providing & fixing in position the following wafer type Butterfly Valves complete with companion flanges, nuts, bolts, gaskets etc. as required. Butterfly valves shall conform to PN-16 rating as per specifications. Quoted price shall be inclusive of insulation as per the specifications.
| a. 250mm dia | No | -- |  | Quote Rate
| b. 200mm dia | No | 3 |  | 0
| c. 150mm dia | No | 15 |  | 0
| d. 125mm dia | No | -- |  | Quote Rate
| e. 100mm dia | No | 4 |  | 0
| f. 80mm dia | No | 14 |  | 0
| g. 65mm dia | No | 18 |  | 0
3.3 | Providing & fixing in position the following Motorised Butterfly Valves with necessary actuator & control wiring. Butterfly valves shall conform to PN-16 rating as per the specifications. Quoted price shall be inclusive of insulation as per the specifications. The valve shall be BMS compatible.
| a. 250mm dia | No | -- |  | Quote Rate
| b. 200mm dia | No | -- |  | Quote Rate
| c. 150mm dia | No | 3 |  | 0
3.4 | Providng and fixing in position the following Ball Valves as per the specifications. Quoted price shall be inclusive of insulation as per the specifications.
| a. 50mm dia | No | 12 |  | 0
| b. 40mm dia | No | 16 |  | 0
| c. 32mm dia | No | 64 |  | 0
| d. 25mm dia | No | 42 |  | 0
| e. 20mm dia | No | -- |  | Quote Rate
3.5 | Providing and fixing in position the following specified make automatic balancing valves. The automatic balancing valves shall conform to PN-16 rating as per the specifications. Quoted price shall be inclusive of insulation as per the specifications.
| a. 150mm dia | No | 3 |  | 0
3.6 | Providing and fixing in position the following specified make balancing valves. The balancing valves shall conform to PN-16 rating as per the specifications. Quoted price shall be inclusive of insulation as per the specifications.
| a. 100mm dia | No | 3 |  | 0
| b. 80mm dia | No | 4 |  | 0
| c. 65mm dia | No | 2 |  | 0
| d. 50mm dia | No | -- |  | Quote Rate
| e . 40mm dia | No | -- |  | Quote Rate
3.7 | Providing and fixing in position self balancing pressure independent two way combined control valves with modulating actuators for AHUs & TFAUs. Quoted price shall be inclusive of cooling/ heating digital thermostat compatible with BMS, and mecessary arrangement to ensure that the valve is 100% closed when AHU/ TFA is shut-off. Valves shall conform to PN-10 rating and shall be complete in all respects as per the specifications. The valves shall be of following sizes:
| a. 150mm dia (398-704 USGPM) | No | -- |  | Quote Rate
| b. 125 mm dia (168-397 USGPM) | No | -- |  | Quote Rate
| c. 100mm dia (123-168 USGPM) | No | 1 |  | 0
| d. 80 mm dia (88-123 USGPM) | No | 2 |  | 0
| e. 65mm dia (56-88 USGPM) | No | 1 |  | 0
| f. 50mm dia (34-56 USGPM) | No | 2 |  | 0
| g. 40mm dia (14-34 USGPM) | No | 6 |  | 0
| h. 32mm dia (7.6-14 USGPM) | No | 31 |  | 0
| i. 25mm dia (4.9-7.5 USGPM) | No | 23 |  | 0
| j. 20mm dia (2.5-4.8 USGPM) | No | -- |  | Quote Rate
3.8 | Providing and fixing in position self balancing pressure independent two way combined control valves with modulating actuators for FCUs. Quoted price shall be inclusive of cooling digital thermostat, copper control wiring in MS conduits, necessary relays to ensure that the valve is 100% closed when FCU is shut-off, and required stepdown transformer. Valves shall conform to PN-10 rating and shall be complete in all respects as per the specifications. The valves shall be of following sizes:
| a. 25mm dia (4.9-7.5 USGPM) | No | 4 |  | 0
| b. 20mm dia (2.5-4.8 USGPM) | No | 57 |  | 0
3.9 | Providing & Fixing in position the following digital cooling only type thermostat compatible with above self balancing pressure independent control valves. The sample shall be approved by ID prior to procurement. | No | 61 |  | 0
3.10 | Providng and fixing in position the following pair of Ball Valves one with strainer and the other without strainer for Fan Coil Units as per the specifications. Quoted price shall be inclusive of insulation.
| a. 25mm dia | No | 4 |  | 0
| b. 20mm dia | No | 57 |  | 0
3.11 | Providing and fixing in position the following wafer type dual plate check valves. Check valves shall conform to PN-16 rating as per the specifications. Quoted price shall be inclusive of insulation as per the specifications.
| a. 200mm dia | No | -- |  | Quote Rate
| b. 150mm dia | No | 6 |  | 0
| d. 100mm dia | No | -- |  | Quote Rate
3.12 | Providing and fixing in position the following 'Y' strainers complete with insulation for AHUs & TFAUs.
| a. 150mm dia | No | -- |  | Quote Rate
| b. 125 mm dia | No | -- |  | Quote Rate
| c. 100mm dia | No | 1 |  | 0
| d. 80 mm dia | No | 2 |  | 0
| e. 65mm dia | No | 1 |  | 0
| f. 50mm dia | No | 2 |  | 0
| g. 40mm dia | No | 6 |  | 0
| h. 32mm dia | No | 31 |  | 0
| i. 25mm dia | No | 23 |  | 0
| j. 20mm dia | No | -- |  | Quote Rate
3.13 | Providing and fixing in position the following automatic purge valves. Purge valves shall conform to PN-16 rating. Quoted price shall be inclusive of isolation valves. | No | 26 |  | 0
3.14 | Providing and fixing in position industrial type pressure gauges constructed out of SS 304 material. SS siphon shall be factory insulated with closed cell elastomeric insulation in tubing form. Pressure gauges shall be factory fitted with a ball valve at the tube. | No | 36 |  | 0
3.15 | Supply and fixing in position V-form industrial type thermometers as per the specifications. | No | 24 |  | 0
3.16 | PRESSURIZATION UNIT WITH BUILT-IN DE-AERATOR
Supply, Installation, Testing & Commissioning of Pressurization Unit with built-in Deaerator consisting of Non-precharged Closed Expansion Tank complete with twin make-up water pumps (including one standby), touchscreen control panel, pressure switch, non-return valve, digital pressure gauges. The tank shall be of black-steel construction and complete as per the specifications. The system shall be capable of degassing air in the system at atmospheric pressure. The unit shall be suitable for the following Capacity and Static Head:
| i. 500 Litres, Static Head 40 M | Nos. | -- |  | Quote Rate
| ii. 300 Litres, Static Head 40 M | Nos. | 1 |  | 0
NOTE: Selection shall be shared based on OEM Standards.
3.17 | DIRT SEPARATORS (CHW)
Supply, Installation, Testing & Commissioning of Dirt Separators for dirt removal including magnetic particles through a ferro magnet. The dirt separator should be able to remove particle sizes upto 5 microns through Copper Mesh, and shall be located on the return CHW line on pump suction. The separator should be complete with flanges, drain valve, and complete as per the specifications. The separator shall be suitable for following flow rate and pressure rating:
| i. 1200 USGPM (PN-10) | Nos. | -- |  | Quote Rate
| ii. 960 USGPM (PN-10) | Nos. | 1 |  | 0
3.18 | VACCUM DEGASSERS
| Supply, Installation, Testing & Commissioning of Vacuum Degasser to be connected as a bypass to the main water pipline in the CHW system. The Vacuum Degasser shall be of automatic operation and fitted with a high efficiency multisatge pump. The degasser shall be of 150 - 300 Cubic Metre degassing capacity with a capacity to degas up to 500 LPH (35 M Static Head) depending upon the model selected as per the system working pressure. The Vacuum Degasser shall be BMS Compatible. | Nos. | 1 |  | 0
3.19 | Providing and fixing in position the following GI medium class pipes for condensate drain cut to required lengths & installed with all screwed joints and providing and fixing position the necessary elbows, tees & reducers.
| a. 50mm dia | RM | 50 |  | 0
| b. 40mm dia | RM | 30 |  | 0
| c. 32mm dia | RM | 30 |  | 0
| d. 25mm dia | RM | 20 |  | 0
| e. 20mm dia | RM | -- |  | Quote Rate
3.2 | Providing, jointing and fixing of uPVC/ CPVC Condensate drain piping with all fittings conforming to IS: 15778:2007 of SDR 11 Grade. Fittings shall include all standard moulded fittings elbows, tees, couplers, reducers, unions, plugs, adaptors with brass threaded insertions and specials. The Solvent Cement for jointing shall be of make and grade as specified by the manufacturer of uPVC/ CPVC piping system. The installation shall be complete in all respects including cutting chases / holes in walls, slabs and making good, etc The entire uPVC/ CPVC piping system shall be installed, tested and commissioned following the recommendation of the manufacturer including provision of expansion loops. All pipework in shafts, ceiling voids and terrace shall be fixed on MS brackets and hangers with U-clamps made from 10 mm dia galvanised steel rod complete with nuts and washers. Cost for MS structural work for supports shall be included in the rates. All horizontal and vertical crossings of building structure (slabs, walls, beams, column etc), the space between pipe and the structure shall be made good and water tight with concrete.
The annular space between the pipe and the sleeves shall be sealed (upto a minimum depth 25 mm) with fire resistant acrylic based sealent of approved make and quality. The pipes shall be painted with two coats of synthetic enamel paint and painting with photoluminescent paint at suitable interval for identification of pipe lines.
Providing and fixing in position the following medium class pipes for condensate drain cut to required lengths & installed with all screwed joints and providing and fixing position the necessary elbows, tees & reducers.
| a. 50mm dia | RM | 20 |  | 0
| b. 40mm dia | RM | 30 |  | 0
| c. 32mm dia | RM | 120 |  | 0
| d. 25mm dia | RM | 150 |  | 0
| e. 20mm dia | RM | 320 |  | 0
3.21 | Supply & Installation of neoprene rubber expansion belows with integral reinforced rubber flanges, guide rods on both sides at inlet and outlet of water chilling/ heating machines, chilled water pumps, of approved make.
| a. 200mm dia | No | -- |  | Quote Rate
| b. 150mm dia | No | 18 |  | 0
| c. 100mm dia | No | -- |  | Quote Rate
3.22 | Providing and fixing in position approved make differential pressure switches complete with copper control wiring between inlet and outlet of each Chillers. These shall be BMS compatible. | Sets | -- |  | Quote Rate
3.23 | Providing and fixing in position the following suction guides with strainer & insulation for chilled water pumps. The suction guides shall be installed at the inlet of each pump and rated for 16 Bar (PN-16) operating pressure. Suction guide shall have SG Iron/ MS body with wall thickness minimum 8mm. Suction guide shall be complete with outlet guide vanes, removable SS strainers and fine mesh SS start-up strainer. The connecting flanges shall be raised face type. Each suction guide shall be provided with 1/2" dia. ball type blow down valve.
| a. 200mm dia | No | -- |  | Quote Rate
| b. 150mm dia | No | 6 |  | 0
3.24 | Providing and fixing in position of approved make Test Points comprising of accessories such as adaptors, needle etc. The test points shall be installed at inlet and outlet of each ceiling suspended AHUs & TFAUs etc. Test points shall be in brass construction and comprise of 1/4" BSP with neoprene sealing bushes and screwed covers. | No | 236 |  | 0
3.25 | BTU METERS FOR AHUs (BMS COMPATIBLE)
Supply, Installation, Testing and Commissioning of BMS compatible ultrasonic BTU Meter complete with flanged type water flow meter (pressure drop across water meter not exceeding 0.1 bar at the specified nominal flow rate), temperature sensors, LCD display panel, inbuilt Lithium battery backup with minimum six years life.
The units shall be capable to calculate and store maximum values, display flow rates and temperature difference across supply and return. The quoted price shall be inclusive of necessary wiring, conduiting between the flow meter and the display panel. The unit shall be housed in a totally tamper proof box. BTU meters shall be capable of providing necessary output on Modbus for BMS integration. The size of the BTU meter is as under:
| a. BTU meter size, 250 mm | No | -- |  | Quote Rate
| b. BTU meter size, 200 mm | No | -- |  | Quote Rate
| c. BTU meter size, 150 mm | No | -- |  | Quote Rate
TOTAL CARRIED TO SUMMARY (CHW PIPING) Rs. |  |  |  |  | 0
4.0 | AIR DISTRIBUTION
4.1 | Ductwork
a. | Factory Fabricated Ductwork
Supply of factory fabricated dutwork, Installation and Testing of galvanised sheet metal ducts including elbows, turning vanes, fire retardant gaskets, slip on flanges, GI fully threaded rods, GI supports/hangers etc. in accordance with the approved shop drawings and specifications. The ducts shall be fabricated and installed in line with SMACNA standards.
| a. 1mm-500mm (26 gauge) GSS | SqM | 2500 |  | 0
| b. 501mm-1050mm (26 gauge) GSS | SqM | 3860 |  | 0
| c. 1051mm-1500mm (24 gauge) GSS | SqM | 2130 |  | 0
| d. 1501mm-1800mm (22 gauge) GSS | SqM | 250 |  | 0
| e. 1801mm-2100mm (20 gauge) GSS | SqM | 150 |  | 0
| f. 2101mm and above (18 gauge) GSS | SqM | 50 |  | 0
b. | Conventional site fabricated ducts using Lock Forming Machines.
Supply, Fabrication, Installation and Testing of sheet metal ducts in accordance with the approved shop drawings and specifications. Ducts shall be fabricated using lock forming machine.
| a. 0.63mm (24 gauge) GSS | SqM | 400 |  | 0
| b. 0.8 mm (22 gauge) GSS | SqM | 100 |  | 0
c. | Supply, Fabrication, Installation & Testing of round sheet metal ducts in accordance with the approved shop drawings and specifications.
| a. 1.0mm (20 gauge) GSS | SqM | 40 |  | 0
d | Supply, Fabrication, Installation and Testing of Powder Coated Eliptical sheet metal ducts in accordance with the approved shop drawings and specifications. All longitudinal and transverse joints should be fully applied with sealants.The joints shall be with least leak and shall be pressure tested. All ducts shall undergo deep cleaning process to remove construction dust prior to testing & commisioning.
| a. 1.0mm (20 gauge) GSS | SqM | 1050 |  | 0
e. | Supply, Fabrication, Installation & Testing of 16 gauge black steel duct work in welded construction. The quoted price shall be inclusive of clean outs as per NFPA at base of verticle riser, change in direction, maximum at every 6.1 M horizontal & every third floor of vertical riser & at sprinkler heads. | SqM | 250 |  | 0
4.2 | Supply, Installation and Testing of 125mm deep Antivibration Flexible Joints made out of imported fire retardant fabric with extruded aluminium frame/ flange on both sides of approved make. | RM | 590 |  | 0
4.3 | Supply, Installation and Testing of multi blade type key operated louver dampers of galvanised steel sheet for collars to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | SqM | 80 |  | 0
4.4 | Supply, Installation and Testing of multiblade box type galvanised steel sheet dampers for ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | SqM | 35 |  | 0
4.5 | Supply, Installation and Testing of multiblade box type galvanised steel sheet dampers for elliptical ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawings and specifications. | Sqm | 20 |  | 0
4.6 | Supply, Installation, Testing & Commissioning of Fire & Smoke dampers as per UL 555 and UL555S with at least 120 minutes fire rating as per the approved shop drawings and specifications. Fire damper shall be motorised spring return type with extended sleeve of 450mm. The dampers shall be of 16G sheet steel construction. The dampers shall be BMS compatible as per the specifications.
| a. Bare Fire & Smoke Dampers | SqM | 15 |  | 0
| b. Spring return type actuator with control panel, temperature sensor and suitable for 10 NM Torque. | No | 30 |  | 0
| c. Spring return type actuator with control panel, temperature sensor and suitable for 16 NM Torque. | No | 10 |  | 0
4.7 | Supply, Installation, Testing & Balancing of square supply air diffusers as per the approved shop drawings and specifications. Each diffuser shall be equipped with fixed air distribution grid, removable key-operated volume control damper. The diffusers shall be anti-smudge ring/ flush type.
Powder coated extruded aluminium diffusers of approved colour & shade of following sizes:
| a. 600x600 diffusers having neck size as mentioned in the "Approved for Construction" shop drawings suitable for fixing in Grid Ceiling. | No | 30 |  | 0
4.8 | Supply, Installation, Testing and Balancing of square diffusers same as supply air diffusers but without volume control dampers for return air as per the approved shop drawings and specifications.
Powder coated extruded aluminium diffusers of approved colour & shade of following sizes:
| a. 600x600 diffusers suitable for fixing in Grid Ceiling. | No | 30 |  | 0
4.9 | Supply, Installation, Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed inner core as per approved shop drawing and specifications. The grilles shall be of approved colour & shade.
a. Powder coated aluminium grille of extruded sections with integral flanges on both sides & ends as required.
| i. 100/150/200 mm High linear Grille | SqM | 50 |  | 0
| i. 100/150/200 mm High Curved Grille | SqM | 20 |  | 0
4.1 | Supply, Installation, Testing and Balancing of multi-slot type linear slot diffusers as per the approved shop drawings and specifications.
a. Powder coated extruded aluminium diffusers of approved colour & shade.
| i. 2/3/4 slot diffusers having width of slots as 25mm. | SqM | 70 |  | 0
4.11 | Supply, Installation, Testing and Commissioning of pre-insulated factory fabricated flexible ducts inner as well as outer skin constructed out of aluminium sheet. Ducts shall be of following sizes:
| a. 200mm dia | RM | 510 |  | 0
| b. 150mm dia | RM | 350 |  | 0
| c. 100mm dia | RM | 200 |  | 0
4.12 | Supply, Installation & Testing of extruded aluminium powder coated air transfer grilles to be provided at toilets & kitchen doors. | SqM | 5 |  | 0
4.13 | Supply, Installation and Testing of fresh air grilles of powder coated/ anodised extruded aluminium with filters, inlet louvers, dampers and bird screen, as per approved shop drawings and specifications. | SqM | 10 |  | 0
4.14 | Supply, Installation and Testing of spigots of different sizes to facilitate flexible duct connection. Quoted price shall be inclusive of necessary clamping arrangement.
| a. 200mm dia | No | 1020 |  | 0
| b. 150mm dia | No | 700 |  | 0
| c. 100mm dia | No | 400 |  | 0
4.15 | Supply, Installation and Testing of non-return dampers as per specifications and design drawings. | SqM | 5 |  | 0
TOTAL CARRIED TO SUMMARY (AIR DISTRIBUTION) Rs. |  |  |  |  | 0
5.0 | INSULATION
5.1 | Supply and Application of internal acoustic/ thermal insulation of ducting using open cell elastomeric insulation with LEED compliant adhesive, longitudinal & transverse joints sealed with adhesive in neat & clean manner. All insulation joints shall have tape of same material with equivalent fire rating as the insulation.
| a. 25 mm thick | SqM | -- |  | Quote Rate
| b. 15 mm thick | SqM | 720 |  | 0
5.2 | Supply and Application of external thermal insulation of ducting using closed cell elastomeric insulation (EPDM) with LEED compliant adhesive, longitudinal & transverse joints sealed with adhesive to form proper bonding. All insulation joints shall have tape of same material with equivalent fire rating as the insulation. No additional remuneration shall be paid for flange insulation.
| a. 16 mm thick | SqM | 5840 |  | 0
| b. 9 mm thick | SqM | 1050 |  | 0
5.3 | Supply and Application of 32mm/25mm/19mm thick closed cell elastomeric insulation in tubing form/ flat sections for chilled water piping to be installed throughout the project as per the specifications.
Quoted price shall be inclusive of adhesive and UV/ Mechanical Protection using weather resistant paint & Glass Cloth/CSM as per specifications.
| a. 300mm dia (32mm thick) | RM | -- |  | Quote Rate
| b. 250mm dia (32mm thick) | RM | -- |  | Quote Rate
| c. 200mm dia (32mm thick) | RM | 180 |  | 0
| d. 150mm dia (32mm thick) | RM | 120 |  | 0
| e. 125mm dia (25mm thick) | RM | 100 |  | 0
| f. 100mm dia (19mm thick) | RM | 110 |  | 0
| g. 80mm dia (19mm thick) | RM | 90 |  | 0
| h. 65mm dia (19mm thick) | RM | 80 |  | 0
| i. 50mm dia (19mm thick) | RM | 100 |  | 0
| j. 40mm dia (19mm thick) | RM | 210 |  | 0
| k. 32mm dia (19mm thick) | RM | 350 |  | 0
| l. 25mm dia (19mm thick) | RM | 250 |  | 0
| m. 20mm dia (19mm thick) | RM | 450 |  | 0
5.4 | Supply and Application of 9 mm thick closed cell elastomeric insulation in tubing form for condensate drain piping as per the specifications.
| a. 50mm dia | RM | 70 |  | 0
| b. 40mm dia | RM | 60 |  | 0
| c. 32mm dia | RM | 150 |  | 0
| d. 25mm dia | RM | 170 |  | 0
| e. 20mm dia | RM | 320 |  | 0
5.5 | Supply and Application of thermal/acoustic lining of walls & ceiling of AHU rooms using fibreglass board having density not less than 80 kg/cu.m, laminated with aluminium foil on one side and three layers of black glass cloth on the other side, mounted on a 610mmx610mm frame work made out of GI sheet channels and as per the specifications.
| a. 25mm thick | SqM | 120 |  | 0
5.6 | Supply and Application of closed cell elastomeric insulation for ducts exposed to atmosphere using 16mm thick insulation material in sheet form with adhesive, and longitudinal & transverse joints sealed with tape of same fire rating as per specifications. Quoted price shall be inclusive of UV/ Mechanical Protection using weather resistant paint & Glass Cloth/CSM as per specifications. | SqM | 530 |  | 0
5.7 | Supply and Application of fire retardant spray, 50mm rockwool and aluminum foil for kitchen hood extract ducts as per the specifications. | SqM | 250 |  | 0
5.8 | Supply and Application Closed cell elastomeric insulation for Roof exposed to sun using 25 mm thick closed cell elastomeric insulation with glass cloth facing (EPDM) material with factory faced glass cloth in sheet form with LEED compliant adhesive, longitudinal & transverse joints sealed with tape of same material as per specifications.
| a. 25 mm thick | SqM | 1250 |  | 0
TOTAL CARRIED TO SUMMARY (INSULATION) Rs. |  |  |  |  | 0
6 | ELECTRICAL
6.1 | MOTOR CONTROL CENTRE
Supply, Installation, Testing and Commissioning of floor mounted cubicle type electrical panel duly powder coated complete with aluminium bus bars, incoming, out going feeders etc. as per specifications, drawings and as described below. The panel shall incorporate an extract fan mounted at the top of the panel complete with thermostat suitable to run the fan at 50 deg C. Fault level 36 kA/1 Sec.
6.1.1 | MCC-1
(LOCATION : PLANT ROOM TERRACE)
INCOMING :
a. | 800 Amps TP+N MCCB EDO type -- 02 Sets
(These breakers should be electrically/ mechanically interlocked.)
b. | Multifunction meter to read ammeter (0 - 800) Amp, Voltmeter (0-500)V, KW and KWH, A set of CT's, RYB LED type phase indication lights -- 02 Sets.
BUSCOUPLER
800 Amps TP+N MCCB EDO type as described above as Bus Coupler - 01 Set.
BUSBARS :
Electrolytic grade (E 91 E), 1000 Amps Capacity TPN aluminium bus bar, PVC heat shrunk insulated, supported on DMC/SMC having fault level of 50 KA for 1 second.
OUTGOING :
a. 315 A TP+N MCCB, digital type ammeter with 630/5A CT's & selector switch for 119 KW motor of 180 TR Screw Chillers with VFD, ON-OFF indication lights --- 03 Sets. (2W+1S)
b. 63 A TP+N MCCB with fully automatic Star/Delta starter with built in single phasing preventer, overload relay & 0-30 seconds adjustable timer, digital type ammeter with CT's & selector switch for 10 HP primary CHW pumps, a set of ON & OFF indication lights & START-STOP push buttons --- 03 Sets. (2W+1S)
c. 100 A TP+N MCCB with fully automatic Star/Delta starter with built in single phasing preventer, overload relay & 0-30 seconds adjustable timer, digital type ammeter with CT's & selector switch for 30 HP CDW pumps, a set of ON & OFF indication lights & START-STOP push buttons --- 03 Sets. (2W+1S)
d. 63 A TP+N MCCB for 20 HP Secondary CHW variable speed pumps, a set of ON & OFF indication lights --- 03 Sets. (2W+1S)
e. 63 A TP+N MCCB with fully automatic DOL starter with built in single phasing preventer, overload relay & 0-30 seconds adjustable timer, digital type ammeter with CT's & selector switch for 15 HP Cooling Tower fan motor, a set of ON & OFF indication lights & START-STOP push buttons --- 03 Sets. (2W+1S)
g. Control wiring & safety circuit as required with Start-Stop PB's stayput or lockable type and LED type 'ON' 'OFF' indication lights.
Notes:
a. Mechanical /electrical interlocking shall be provided between chillers, Heat Pumps, pumps and cooling towers as per system requirement briefly described below in order of operation:
i. CDW Pump
ii. CT Fan
iii. P CHW Pump
iv. S CHW Pump
v. Chiller
NOTE: BMS/ CPM shall supercede interlocking at panel level.
b. MCC should have enough space for mounting of VFDs within panel as required for Chiller, secondary chilled water pumps and shall have adequate ventilation arrangement for the same.
| MCC as described above. | No | 1 |  | 0
6.2 | ELECTRICAL PANELS FOR Air Waser/ EFS/AXIAL / etc.
Supply, Installation, Testing & Commissioning of wall/floor mounted cubicle type electrical panels including system control wiring with incoming, outgoing feeders as described below and as per specifications.
6.2.1 | PANEL-'A' (LPP-3 & LPP- 4) (F&B TFA-4) (EFS-1)
Location : Close to Units
a. 40A 4P MCB for 7.5 / 5 HP motor - 01 Set.
b. RYB LED type indication lights --- 01 Set.
c. Auto-Manual type selector switch to facilitate auto start of fans after restoration of power -- 01 Set.
d. Control wiring & safety circuit as required with Start-Stop PB's stayput or lockable type and LED type 'ON' 'OFF' indication lights.
| Electrical panels as described above. | No | 4 |  | 0
6.2.2 | PANEL-'B' (SEFP-1,6,7,8,9,10,12,13 & 14)
Location : Close to Units
INCOMING :
a. 20A 4P MCB --- 01 Set.
b. RYB LED type indication lights --- 01 Set.
c. Digital Type Voltmeter (0-500)V --- 01 Set.
BUSBARS :
Electrolytic grade (E 91 E), 25 A capacity TPN aluminium busbar, PVC heat shrunk insulated, supported on DMC/SMC having fault level of 25 KA for 1 second.
OUTGOING :
a. 16A TP MCB for 2/ 3 HP motor, a fully automatic DOL starter with built in single phasing preventer and overload relay, a set of LED type ON & OFF indication lights & START- STOP push buttons -02 sets.
b. Auto-Manual type selector switch to facilitate auto start of fans after restoration of power -- 02 Sets.
c. Control wiring & safety circuit as required with Start-Stop PB's stayput or lockable type and LED type 'ON' 'OFF' indication lights.
| Electrical panels as described above. | No | 9 |  | 0
6.2.3 | PANEL-'C' (SEFP-2,3,4,5,11) + (LPP-2)
Location : Close to Units
INCOMING :
a. 63A TP+N MCB --- 01 Set.
b. RYB LED type indication lights --- 01 Set.
c. Digital Type Voltmeter (0-500)V --- 01 Set.
BUSBARS :
Electrolytic grade (E 91 E), 100 A capacity TPN aluminium busbar, PVC heat shrunk insulated, supported on DMC/SMC having fault level of 25 KA for 1 second.
OUTGOING :
a. 40A TP MCB for 7.5 /5 HP motor, a fully automatic DOL starter with built in single phasing preventer and overload relay, a set of LED type ON & OFF indication lights & START- STOP push buttons -02 set.
b. Auto-Manual type selector switch to facilitate auto start of fans after restoration of power -- 02 Sets.
c. Control wiring & safety circuit as required with Start-Stop PB's stayput or lockable type and LED type 'ON' 'OFF' indication lights.
| Electrical panels as described above. | No | 6 |  | 0
6.2.4 | PANEL-'D' (LPP-1)
Location : Close to Units
INCOMING :
a. 63A TP+N MCB --- 01 Set.
b. RYB LED type indication lights --- 01 Set.
c. Digital Type Voltmeter (0-500)V --- 01 Set.
BUSBARS :
Electrolytic grade (E 91 E), 100 A capacity TPN aluminium busbar, PVC heat shrunk insulated, supported on DMC/SMC having fault level of 25 KA for 1 second.
OUTGOING :
a. 40A TP MCB for 5 HP motor, a fully automatic DOL starter with built in single phasing preventer and overload relay, a set of LED type ON & OFF indication lights & START- STOP push buttons -04 set.
b. Auto-Manual type selector switch to facilitate auto start of fans after restoration of power -- 04 Sets.
c. Control wiring & safety circuit as required with Start-Stop PB's stayput or lockable type and LED type 'ON' 'OFF' indication lights.
| Electrical panels as described above. | No | 1 |  | 0
Note:
1. The fabricator shall have the busbar chamber tested & approved at CPRI for 50 KA/1 Sec.
2. The outgoing starter feeders for ventilation fans shall be provided with push buttons, indicating lamps for status indication.
3. Proper isolation switches to be provided near air supply and extract fans.
4. Bimetal overload relay for all the starters shall have built-in single phasing prevention feature.
5. Electrical interlocking wiring shall be provided as per system requirement.
6. Power cabling/wiring with necessary earthing from source to each panel shall be provided by other agencies.
7. All Electrical Panels shall be compatible with BMS and necessary provisions to be made in each panel.
6.3 | POWER CABLING
Supply, laying, affecting connections & Testing of the following sizes of 1.1 KV armoured PVC insulated aluminium/ copper conductor cables. Cables shall be inclusive conductor cables. Cables shall be inclusive of all clamps, saddles, screws, cable identification tags, cable terminal joints including terminal lugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required.
Normal Cables
| a. 3.5C x 240 Sqmm cable (Aluminium) | RM | 120 |  | 0
| b. 3.5C x 150 Sqmm cable (Aluminium) | RM | -- |  | Quote Rate
| c. 3.5C x 120 Sqmm cable (Aluminium) | RM | -- |  | Quote Rate
| d. 3.5C x 95 Sqmm cable (Aluminium) | RM | -- |  | Quote Rate
| e. 3C x 35 Sqmm cable (Aluminium) | RM | 110 |  | 0
| f. 3C x 25 Sqmm cable (Aluminium) | RM | 50 |  | 0
| g. 3C x 16 Sqmm cable (Copper) | RM | 280 |  | 0
| h. 3C x 10 Sqmm cable (Copper) | RM | 180 |  | 0
| i. 3C x 6 Sqmm cable (Copper) | RM | 200 |  | 0
| j. 3C x 4 Sqmm cable (Copper) | RM | 50 |  | 0
| k. 3C x 2.5 Sqmm cable (Copper) | RM | 150 |  | 0
FRLS Cables - For Fire & Life Safety Equipments
| a. 4 C x 10 Sqmm cable (Copper) | RM | 80 |  | 0
| a. 4 C x 6 Sqmm cable (Copper) | RM | 180 |  | 0
| a. 4 C x 4 Sqmm cable (Copper) | RM | 310 |  | 0
| b. 4C x 2.5 Sqmm cable (Copper) | RM | -- |  | Quote Rate
6.4 | CABLE TRAYS
Supplying & Fixing of following sizes of GI cable tray duly painted perforated type along with necessary elbows, bends, reducers etc. anchored along the wall / suspended from the ceiling with necessary MS supports. Supports shall be in the form of 40mmx40mmx5mm angles and provided at a distance of 1200mm including grouting in the wall and making good as well.
| a. 40 x 50 x 40 x 2mm | RM | -- |  | Quote Rate
| b. 40 x 100 x 40 x 2mm | RM | 500 |  | 0
| c. 40 x 150 x 40 x 2mm | RM | 300 |  | 0
| d. 40 x 300 x 40 x 2mm | RM | 250 |  | 0
| e. 40 x 450 x 40 x 2mm | RM | 150 |  | 0
| f. 40 x 600 x 40 x 2mm | RM | -- |  | Quote Rate
6.5 | EARTHING
Providing & fixing in position the following bare GI tape/ Cu wire including providing all fixing accessories & effecting proper connections.
| a. 2x 32mm x 6mm tape | RM | 150 |  | 0
| b. 2x 25mm x 3mm tape | RM | 100 |  | 0
| c. 8 SWG Cu Wire | RM | 3250 |  | 0
| d. 12 SWG Cu Wire | RM | -- |  | Quote Rate
6.6 | Supply and Installation of TPN isolator of appropriate rating in weather proof enclosure near cooling towers. | No | 4 |  | 0
6.7 | Supply and fixing of 1.1 KV grade rubber mat 914.4 mm wide 6mm thick to withstand 1.1 KV dielectric strength in front of each panel. | RM | 15 |  | 0
TOTAL CARRIED TO SUMMARY (ELECTRICAL) Rs. |  |  |  |  | 0
Notes:
1. GST extra @18% on the total contract value.
2. Duty exemption under EPCG scheme to be considered on the following items:
Import Duty
1. Water Cooled Screw Chillers
2. Fan Coil Units
3. Variable Frequency Drives
4. Self Balancing Pressure Independent Control Valves

## Schedule Of Quantities
PRICED SCHEDULE OF QUANTITIES
SUMMARY OF COSTS
ITEM | DESCRIPTION |  |  | AMOUNT (Rs.)
1. | EQUIPMENT |  |  | 0
TOTAL SUMMARY OF COSTS (INR) |  |  |  | 0
ITEM | DESCRIPTION | UNIT | QTY. | RATE | AMOUNT
1.0 | EQUIPMENT
1.1 | WATER COOLED SCREW CHILLERS
1.1.1 | Supply, Installation, Testing & Commissioning of AHRI certified water cooled chiller package of 180 TR actual capacity with unit mounted Air Cooled VFD with IP-55 protection (without AHF), comprising of helical rotary compressor/s with direct drive motor (the compressor speed shall not exceed 3000 RPM), insulated shell and tube type plain tube chiller as well as shell & tube type integrally finned condenser. The chiller package shall also be complete with vibration isolation mountings, copper refrigerant piping, full refrigerant charge, system control wiring and accessories as required. The chiller package shall be installed on a fabricated mild steel base frame assembled to form a compact assembly. The chiller package shall also be complete with microprocessor based control panel comprising of all adaptive controls, indication lights, VFD starter, over load and under load protection, TPN isolator for termination of incoming power cable, necessary control wiring, disconnect switch, mechanical couplings at in and out of both heat exchangers, DP switches for both heat exchangers & vibration isolation arrangement all complete as per the specifications.
The motor shall be suitable for operation on 415 ± 10% volts, 50 Hz, 3 Phase, AC power supply. The chiller package shall be BMS compatible. The water cooled screw chillers shall meet the following design parameters:
a. Chilled water leaving
temperature : 44 F (6.7 C)
b. Chilled water entering
temperature : 54 F (12.2 C)
c. Chiller fouling factor : 0.0005 sft.hr.F/BTU
d. Condenser water entering
temperature : 88 F (31.1 C)
e. Condenser water leaving
temperature : 98 F (36.6 C)
f. Condenser fouling factor : 0.001 sft.hr.F/BTU
g. Type of Refrigerant : R-134a
h. Certification : AHRI
i. Chiller and Condenser : 150 PSIG
Minimum Pressure Rating
j. Maximum permissible
IKW/TR at full load : 0.63
| k. Minimum COP : 5.9 |  |  |  | One more chiller will be install in future
l. Minimum NPLV : 0.37
m. Minimum IPLV : 0.36
| Water cooled screw chillers as described above. | No | 2 |  | 0
1.1.2 | Clearance of chillers at nearest Port, Insurance Cover, Transportation to site at Chandigarh. Handling of chillers, lifting & shifting upto foundation on Terrace , positioning on foundation, Installation, Testing and Commissioning. | No | 2 |  | Included Above
(Chilled water connections and cable termination at each chiller package shall be carried out by Low side vendor in co-ordination with the chiller manufacturer.)
Notes:
1. Bidders shall ensure availability of spare parts for chillers for a minimum period of Ten Years.
2. Quoted price shall be For site.
TOTAL CARRIED TO SUMMARY (EQUIPMENT) Rs. |  |  |  |  | 0